## Instructions
NRM1 ORDER OF COST ESTIMATE TOOL ¦ Estates AI ¦ Version 2.0 ¦ May 2026
RIBA Stage 0–1 Indicative Estimates ¦ Prepared by Nabil Kayali ¦ Base date Q2 2026 ¦ West Midlands default
WHAT'S NEW IN VERSION 2.0
▸ Mid-point rate architecture — each element now has a single benchmark mid-point (£/m²) with ±spread applied automatically
▸ Tighter 20-25% spread (Low–High range) replacing the previous wide ranges that were not useful for feasibility reporting
▸ Three specification levels per project type — Basic, Standard, High Spec — each on a separate tab
▸ Rates Reference Table tab — all benchmark mid-point rates in one place; update here and all tabs recalculate
▸ BCIS-traceable structure — rate cells reference a named source column; when a BCIS subscription is obtained, update the Rates Table
SPECIFICATION LEVELS — WHICH TAB TO USE
Level 1 — Basic / Maintenance: Like-for-like replacement, redecoration, basic M&E refresh. No layout change. Functional finish only.
Level 2 — Standard / Cat A–B: Modified layout, new M&E distribution, Cat A or Cat B office/teaching finish. Most university estates projects.
Level 3 — High Spec / Specialist: Flagship, lab, healthcare, or bespoke. Heavy M&E, specialist fit-out, feature finishes. Premium.
HOW TO USE THIS WORKBOOK
1. Select the tab for your project type and specification level.
2. Update the GIFA (m²) — yellow input cell at the top of the tab. All totals recalculate instantly.
3. Update the BCIS Location Factor — yellow input cell. See the BCIS Factors tab for your region.
4. Adjust the Spread % if needed (default 22% gives approx ±11% around the mid-point).
5. Review each element. Adjust mid-point rates in the Rates Reference Table if you have better local data.
6. Adjust the Additions section (Prelims, Fees, Risk) using the signal rules shown in the Notes column.
7. The Total Project Cost (excl. VAT) calculates automatically. VAT is shown separately for reference only.
HOW TO UPDATE RATES WHEN BCIS DATA IS AVAILABLE
All benchmark mid-point rates sit in the Rates Reference Table tab (columns E–L).
Each cell in that table is the single source of truth for the estimate tabs — update the table, all tabs update.
Recommended update frequency: quarterly (align with BCIS Quarterly Review of Building Prices).
When BCIS subscription is obtained: replace mid-point rates with BCIS elemental benchmarks for your building type and region.
Record the BCIS edition/date in the Source column of the Rates Table — this creates an audit trail.
COLOUR CODING
Yellow cells = User input — GIFA, BCIS factor, Spread %, individual rate overrides
Blue cells = Calculated values from rates table (do not edit directly — update rates table instead)
Green rows = Subtotals and Total Project Cost
Amber rows = Risk Allowance — must be built from project risk register signals
Teal rows = Client Contingency — always fixed at 5%
Grey rows = Elements excluded for this project type
Orange/red rows = VAT (reference only) and Disclaimer
⚠ MANDATORY DISCLAIMER
This Order of Cost Estimate is INDICATIVE ONLY, produced at RIBA Stage 0–1 without measured quantities or detailed design.
Rates are based on £/m² benchmarks cross-referenced against Q2 2026 market data (RICS/BCIS published ranges).
This estimate MUST be reviewed and validated by a Chartered Quantity Surveyor before use in any business case or budget approval.
All figures are LOW–HIGH ranges only. No single-point estimates are shown. Rates should be updated against BCIS data before formal use.

## Rates Reference Table
RATES REFERENCE TABLE — Mid-point £/m² GIFA Benchmark Rates ¦ Q2 2026 ¦ UK National Mean ¦ Update this table to refresh all estimate tabs
Source: Sense-checked against RICS/BCIS published ranges Q4 2025–Q2 2026, Cushman & Wakefield UK Fit-Out Guide 2025, RateQS benchmarks Nov 2025. All rates are mid-point estimates at UK national mean. Apply BCIS regional factor in estimate tabs. Update quarterly when BCIS subscription is available.
Grp | Sub | Element / Description | Unit | Rfb Basic | Rfb Standard | Rfb High Spec | New Build Standard | New Build High Spec | Extension Standard | Extension High Spec | External Works Only | Notes / Rate Driver
GROUP 0 — FACILITATING WORKS — Include if demolition, known asbestos, or brownfield site identified in questionnaire
0 | 0.1 | Toxic/hazardous material removal | Item | 15 | 25 | 40 | 10 | 20 | 10 | 20 | 0 | Asbestos; increase if confirmed present (refurb/demo only)
0 | 0.2 | Demolition & structural alterations | Item | 20 | 35 | 55 | 15 | 25 | 20 | 35 | 5 | Selective or full demolition; structural openings
0 | 0.3 | Contaminated land remediation | Item | 5 | 10 | 20 | 10 | 20 | 5 | 15 | 10 | Brownfield/contaminated; specialist quote needed
0 | 0.4 | Ground stabilisation | Item | 5 | 8 | 15 | 8 | 15 | 5 | 12 | 5 | Underpinning/piling if ground risk identified
GROUP 1 — SUBSTRUCTURE — New build and extension only; always exclude for pure refurb/fit-out
1 | 1.1 | Standard foundations (strip/pad) | m² | 0 | 0 | 0 | 55 | 80 | 55 | 80 | 0 | New build only; included in Group 7 rate for extensions
1 | 1.2 | Specialist foundations (piled) | m² | 0 | 0 | 0 | 40 | 60 | 40 | 60 | 0 | Poor ground conditions; trigger from GI report
1 | 1.3 | Lowest floor construction (slab) | m² | 0 | 0 | 0 | 35 | 55 | 35 | 55 | 0 | Ground bearing or suspended; inc DPM and insulation
1 | 1.4 | Basement excavation & structure | Item | 0 | 0 | 0 | 80 | 150 | 80 | 150 | 0 | High uncertainty; specialist estimate recommended
GROUP 2 — SUPERSTRUCTURE — Core element for new build; partial inclusion for extension/refurb with structural alterations
2 | 2.1 | Structural frame | m² | 0 | 20 | 40 | 150 | 220 | 130 | 200 | 0 | Steel/concrete/timber; new build or major extensions only
2 | 2.2 | Upper floors | m² | 0 | 15 | 30 | 65 | 95 | 65 | 95 | 0 | New build or added floors; inc topping and insulation
2 | 2.3 | Roof structure & covering | m² | 35 | 55 | 90 | 75 | 120 | 75 | 120 | 0 | New or replacement; inc insulation, waterproofing, rainwater
2 | 2.4 | Stairs & ramps | Item | 10 | 15 | 25 | 20 | 35 | 20 | 35 | 0 | RC, steel or timber; accessibility ramps
2 | 2.5 | External walls & facade | m² | 30 | 60 | 110 | 200 | 320 | 180 | 280 | 0 | Masonry/cladding; refurb = overcladding or repair only
2 | 2.6 | Windows & external doors | m² | 80 | 130 | 200 | 100 | 160 | 90 | 150 | 0 | uPVC (low) to aluminium curtain wall (high)
2 | 2.7 | Internal walls & partitions | m² | 20 | 35 | 60 | 30 | 50 | 25 | 45 | 0 | Blockwork, drywall or glazed; do not double-count Grp 3
2 | 2.8 | Internal doors & ironmongery | Nr | 15 | 25 | 40 | 20 | 35 | 18 | 30 | 0 | Fire-rated at upper range; standard at lower
GROUP 3 — INTERNAL FINISHES ★ ALWAYS INCLUDED — NEVER excluded — every project has internal finishes to some level
3 | 3.1 | Wall finishes | m² | 15 | 35 | 75 | 25 | 55 | 20 | 50 | 0 | Emulsion (low) → specialist tiling/feature panelling (high)
3 | 3.2 | Floor finishes | m² | 20 | 55 | 130 | 30 | 80 | 25 | 70 | 0 | Vinyl/carpet (low) → stone/raised access floor (high)
3 | 3.3 | Ceiling finishes | m² | 10 | 30 | 65 | 15 | 45 | 12 | 40 | 0 | Emulsion (low) → bespoke acoustic ceiling system (high)
GROUP 4 — FITTINGS, FURNISHINGS & EQUIPMENT — Include if joinery, kitchens, toilets or specialist fit-out selected in Q2.2
4 | 4.1 | General fittings & built-in joinery | Item | 10 | 30 | 80 | 15 | 50 | 10 | 40 | 0 | Reception desks, shelving, built-in furniture
4 | 4.2 | Sanitary fittings & toilet fit-out | Nr | 8 | 18 | 35 | 10 | 22 | 8 | 18 | 0 | WC packs; uplift for accessible/changing facilities
4 | 4.3 | Kitchen / break-out area | Item | 5 | 15 | 35 | 8 | 20 | 5 | 15 | 0 | Fitted units, worktops, appliances
4 | 4.4 | Specialist equipment (lab/AV/med) | Item | 0 | 10 | 80 | 5 | 60 | 0 | 40 | 0 | Laboratory, medical, AV; confirm with specialist
GROUP 5 — MECHANICAL & ELECTRICAL SERVICES ★ KEY ELEMENT — Always price separately — never bundle into superstructure rate
5 | 5.1 | Sanitary plumbing (1st & 2nd fix) | m² | 15 | 35 | 65 | 25 | 50 | 20 | 45 | 0 | HWS, cold water, drainage connections
5 | 5.2 | Heating & hot water (LTHW/heat pump) | m² | 25 | 50 | 90 | 35 | 70 | 30 | 65 | 0 | LTHW system or heat pump; include buffer vessel
5 | 5.3 | Ventilation & air handling | m² | 20 | 45 | 90 | 30 | 70 | 25 | 60 | 0 | MVHR/AHU; uplift for lab/healthcare extract (+50-100%)
5 | 5.4 | Air conditioning & cooling | m² | 0 | 30 | 70 | 15 | 55 | 10 | 45 | 0 | VRF/splits; omit if not in scope
5 | 5.5 | Gas installation | Item | 5 | 10 | 15 | 8 | 15 | 5 | 10 | 0 | Omit if all-electric; confirm with utility
5 | 5.6 | Sprinkler / fire suppression | m² | 0 | 15 | 30 | 10 | 25 | 5 | 20 | 0 | >18m height or insurer requirement
5 | 5.7 | Electrical distribution & switchgear | m² | 15 | 30 | 55 | 20 | 45 | 15 | 40 | 0 | LV panels, distribution boards, earthing, containment
5 | 5.8 | Electrical wiring (1st & 2nd fix) | m² | 20 | 40 | 75 | 30 | 60 | 25 | 55 | 0 | All power and lighting circuits; inc containment
5 | 5.9 | Emergency lighting & fire alarm | m² | 10 | 20 | 35 | 12 | 25 | 10 | 22 | 0 | L2 minimum; upgrade for multi-zone/complex layouts
5 | 5.10 | External lighting | Item | 0 | 5 | 10 | 5 | 12 | 3 | 8 | 10 | Column/wall-mounted perimeter lighting
5 | 5.11 | Solar PV / renewables | kWp | 0 | 800 | 1200 | 800 | 1200 | 800 | 1200 | 0 | £/kWp installed; coordinate structural loading + electrical
5 | 5.12 | EV charging points | Nr | 0 | 1500 | 2500 | 1500 | 2500 | 1500 | 2500 | 2000 | Per charge point inc groundworks; 7kW fast charger
5 | 5.13 | IT / data infrastructure (Cat6A) | m² | 8 | 18 | 35 | 10 | 25 | 8 | 20 | 0 | Cabling, containment, patch panels
5 | 5.14 | AV systems | Item | 0 | 10 | 50 | 5 | 40 | 3 | 30 | 0 | Lecture rooms, boardrooms; specialist-designed
5 | 5.15 | Access control & CCTV / security | m² | 5 | 15 | 30 | 8 | 20 | 5 | 15 | 0 | Door access readers, CCTV; varies by security level
5 | 5.16 | Lifts & platform lifts | Nr | 50 | 80 | 120 | 60 | 100 | 50 | 90 | 0 | Per installation × Nr; inc shaft if new build
5 | 5.17 | Builder's work in connection (BWIC) | m² | 5 | 12 | 22 | 8 | 18 | 6 | 15 | 0 | Penetrations, plinths, ducts, concrete bases for plant
GROUP 6 — PREFABRICATED / MODULAR (if applicable) — Exclude if not applicable; specialist contractor quote always required
6 | 6.1 | Prefabricated / modular units | Item | 0 | 0 | 200 | 0 | 150 | 0 | 100 | 0 | Factory-built modular; specialist quote required
6 | 6.2 | Pre-engineered systems (mezzanine) | Item | 0 | 50 | 100 | 0 | 80 | 0 | 60 | 0 | Mezzanine floors, demountable partitions
GROUP 7 — WORK TO EXISTING BUILDINGS — Refurbishment and extension only; +15-25% rate uplift for pre-1900 or listed buildings
7 | 7.1 | Structural repairs | Item | 10 | 25 | 55 | 0 | 0 | 15 | 35 | 0 | Crack stitching, bearing repairs; increase for poor condition
7 | 7.2 | Fabric / envelope repairs | Item | 10 | 20 | 45 | 0 | 0 | 12 | 28 | 0 | Repointing, waterproofing, weathertight works
7 | 7.3 | Damp proof course treatment | Item | 5 | 10 | 20 | 0 | 0 | 5 | 15 | 0 | Chemical DPC; increase for severe rising damp
7 | 7.4 | M&E overhaul / life-expired services | Item | 0 | 30 | 80 | 0 | 0 | 20 | 55 | 0 | Replacement of end-of-life mechanical & electrical plant
7 | 7.5 | Making good after structural works | Item | 5 | 10 | 20 | 0 | 0 | 5 | 12 | 0 | Patch plaster, redecoration after structural alterations
GROUP 8 — EXTERNAL WORKS — Always include; External Works tab uses these as primary cost driver
8 | 8.1 | Site preparation & clearance | Item | 3 | 8 | 15 | 8 | 18 | 5 | 12 | 10 | Strip topsoil, vegetation, temp fencing and hoarding
8 | 8.2 | Roads, paths & hard paving | m² | 0 | 10 | 20 | 15 | 35 | 10 | 25 | 35 | Macadam/block paving; inc edging and drainage channels
8 | 8.3 | Car parking (line-marked bays) | Nr | 0 | 5 | 10 | 5 | 12 | 3 | 8 | 20 | Surfacing, line markings, disabled bays
8 | 8.4 | Surface water drainage | Item | 3 | 8 | 15 | 10 | 20 | 5 | 15 | 25 | Gullies, pipes, SuDS if required by planning
8 | 8.5 | Foul drainage connections | Item | 3 | 6 | 12 | 8 | 15 | 5 | 10 | 15 | Connection to existing drain or new manhole
8 | 8.6 | External utility services | Item | 3 | 8 | 15 | 10 | 20 | 5 | 15 | 20 | Gas/water/electric diversions; early check with DNO
8 | 8.7 | Soft landscaping | m² | 0 | 3 | 8 | 5 | 12 | 3 | 10 | 15 | Planting, seeding, topsoil reinstatement
8 | 8.8 | Boundary enclosures (fences/gates) | Item | 0 | 3 | 8 | 3 | 10 | 2 | 8 | 12 | Security fencing, gates, boundary walls, railings
8 | 8.9 | External lighting | Item | 0 | 2 | 5 | 3 | 8 | 2 | 6 | 10 | Column or wall-mounted lighting (see also 5.10)
UPDATE LOG: Version 2.0 — May 2026 — Rates sense-checked against: BCIS Q4 2025 index (+5% from Q4 2024); RICS new build £1,800–£2,500/m² national (standard-good spec); Cushman & Wakefield Cat B office £800–£1,300/m² national; RapidQS commercial fit-out £800–£2,500/m²; K2 Space/Fusion office fit-out £500–£1,300/m² national. Next review due: Q4 2026. When BCIS subscription obtained, replace rates above with BCIS elemental benchmarks.

## Rfb – Basic
NRM1 ESTIMATE — REFURB / FIT-OUT — BASIC / MAINTENANCE
Spec level: Like-for-like replacement, redecoration, basic M&E refresh. No layout changes. ¦ RIBA Stage 0–1 indicative only ¦ Base date Q2 2026
Project Type: | Refurb / Fit-Out |  | Spec Level: | Basic / Maintenance |  | Region: | West Midlands
GIFA (m²) ▼ update: | 500 |  | BCIS Location Factor ▼: | 94% |  | Spread ±% ▼: | 22%
Grp | Sub | Element / Description | Unit | Mid-Point £/m² | Low £/m² | High £/m² | Total LOW (£) | Total HIGH (£) | Notes / Rate Driver
GROUP 0 — FACILITATING WORKS
0 | 0.1 | Toxic/hazardous material removal | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Asbestos; increase if confirmed present (refurb/demo only)
0 | 0.2 | Demolition & structural alterations | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Selective or full demolition; structural openings
0 | 0.3 | Contaminated land remediation | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Brownfield/contaminated; specialist quote needed
0 | 0.4 | Ground stabilisation | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Underpinning/piling if ground risk identified
GROUP 1 — SUBSTRUCTURE
1 | 1.1 | Standard foundations (strip/pad) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | New build only; included in Group 7 rate for extensions
1 | 1.2 | Specialist foundations (piled) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Poor ground conditions; trigger from GI report
1 | 1.3 | Lowest floor construction (slab) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Ground bearing or suspended; inc DPM and insulation
1 | 1.4 | Basement excavation & structure | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | High uncertainty; specialist estimate recommended
GROUP 2 — SUPERSTRUCTURE
2 | 2.1 | Structural frame | m² | 0 | 0 | 0 | 0 | 0 | Steel/concrete/timber; new build or major extensions only
2 | 2.2 | Upper floors | m² | 0 | 0 | 0 | 0 | 0 | New build or added floors; inc topping and insulation
2 | 2.3 | Roof structure & covering | m² | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | New or replacement; inc insulation, waterproofing, rainwater
2 | 2.4 | Stairs & ramps | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | RC, steel or timber; accessibility ramps
2 | 2.5 | External walls & facade | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | Masonry/cladding; refurb = overcladding or repair only
2 | 2.6 | Windows & external doors | m² | 75.2 | 66.928 | 83.472 | 33464 | 41736 | uPVC (low) to aluminium curtain wall (high)
2 | 2.7 | Internal walls & partitions | m² | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Blockwork, drywall or glazed; do not double-count Grp 3
2 | 2.8 | Internal doors & ironmongery | Nr | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Fire-rated at upper range; standard at lower
GROUP 3 — INTERNAL FINISHES ★ ALWAYS INCLUDED
3 | 3.1 | Wall finishes | m² | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Emulsion (low) → specialist tiling/feature panelling (high)
3 | 3.2 | Floor finishes | m² | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Vinyl/carpet (low) → stone/raised access floor (high)
3 | 3.3 | Ceiling finishes | m² | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Emulsion (low) → bespoke acoustic ceiling system (high)
GROUP 4 — FITTINGS, FURNISHINGS & EQUIPMENT
4 | 4.1 | General fittings & built-in joinery | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Reception desks, shelving, built-in furniture
4 | 4.2 | Sanitary fittings & toilet fit-out | Nr | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | WC packs; uplift for accessible/changing facilities
4 | 4.3 | Kitchen / break-out area | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Fitted units, worktops, appliances
4 | 4.4 | Specialist equipment (lab/AV/med) | Item | 0 | 0 | 0 | 0 | 0 | Laboratory, medical, AV; confirm with specialist
GROUP 5 — MECHANICAL & ELECTRICAL SERVICES ★ KEY ELEMENT
5 | 5.1 | Sanitary plumbing (1st & 2nd fix) | m² | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | HWS, cold water, drainage connections
5 | 5.2 | Heating & hot water (LTHW/heat pump) | m² | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | LTHW system or heat pump; include buffer vessel
5 | 5.3 | Ventilation & air handling | m² | 18.8 | 16.732 | 20.868 | 8366 | 10434 | MVHR/AHU; uplift for lab/healthcare extract (+50-100%)
5 | 5.4 | Air conditioning & cooling | m² | 0 | 0 | 0 | 0 | 0 | VRF/splits; omit if not in scope
5 | 5.5 | Gas installation | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Omit if all-electric; confirm with utility
5 | 5.6 | Sprinkler / fire suppression | m² | 0 | 0 | 0 | 0 | 0 | >18m height or insurer requirement
5 | 5.7 | Electrical distribution & switchgear | m² | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | LV panels, distribution boards, earthing, containment
5 | 5.8 | Electrical wiring (1st & 2nd fix) | m² | 18.8 | 16.732 | 20.868 | 8366 | 10434 | All power and lighting circuits; inc containment
5 | 5.9 | Emergency lighting & fire alarm | m² | 9.4 | 8.366 | 10.434 | 4183 | 5217 | L2 minimum; upgrade for multi-zone/complex layouts
5 | 5.10 | External lighting | Item | 0 | 0 | 0 | 0 | 0 | Column/wall-mounted perimeter lighting
5 | 5.11 | Solar PV / renewables | kWp | 0 | 0 | 0 | 0 | 0 | £/kWp installed; coordinate structural loading + electrical
5 | 5.12 | EV charging points | Nr | 0 | 0 | 0 | 0 | 0 | Per charge point inc groundworks; 7kW fast charger
5 | 5.13 | IT / data infrastructure (Cat6A) | m² | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Cabling, containment, patch panels
5 | 5.14 | AV systems | Item | 0 | 0 | 0 | 0 | 0 | Lecture rooms, boardrooms; specialist-designed
5 | 5.15 | Access control & CCTV / security | m² | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Door access readers, CCTV; varies by security level
5 | 5.16 | Lifts & platform lifts | Nr | 47 | 41.83 | 52.17 | 20915 | 26085 | Per installation × Nr; inc shaft if new build
5 | 5.17 | Builder's work in connection (BWIC) | m² | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Penetrations, plinths, ducts, concrete bases for plant
GROUP 6 — PREFABRICATED / MODULAR (if applicable)
6 | 6.1 | Prefabricated / modular units | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Factory-built modular; specialist quote required
6 | 6.2 | Pre-engineered systems (mezzanine) | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Mezzanine floors, demountable partitions
GROUP 7 — WORK TO EXISTING BUILDINGS
7 | 7.1 | Structural repairs | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Crack stitching, bearing repairs; increase for poor condition
7 | 7.2 | Fabric / envelope repairs | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Repointing, waterproofing, weathertight works
7 | 7.3 | Damp proof course treatment | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Chemical DPC; increase for severe rising damp
7 | 7.4 | M&E overhaul / life-expired services | Item | 0 | 0 | 0 | 0 | 0 | Replacement of end-of-life mechanical & electrical plant
7 | 7.5 | Making good after structural works | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Patch plaster, redecoration after structural alterations
GROUP 8 — EXTERNAL WORKS
8 | 8.1 | Site preparation & clearance | Item | 2.82 | 2.5098 | 3.1302 | 1254.9 | 1565.1 | Strip topsoil, vegetation, temp fencing and hoarding
8 | 8.2 | Roads, paths & hard paving | m² | 0 | 0 | 0 | 0 | 0 | Macadam/block paving; inc edging and drainage channels
8 | 8.3 | Car parking (line-marked bays) | Nr | 0 | 0 | 0 | 0 | 0 | Surfacing, line markings, disabled bays
8 | 8.4 | Surface water drainage | Item | 2.82 | 2.5098 | 3.1302 | 1254.9 | 1565.1 | Gullies, pipes, SuDS if required by planning
8 | 8.5 | Foul drainage connections | Item | 2.82 | 2.5098 | 3.1302 | 1254.9 | 1565.1 | Connection to existing drain or new manhole
8 | 8.6 | External utility services | Item | 2.82 | 2.5098 | 3.1302 | 1254.9 | 1565.1 | Gas/water/electric diversions; early check with DNO
8 | 8.7 | Soft landscaping | m² | 0 | 0 | 0 | 0 | 0 | Planting, seeding, topsoil reinstatement
8 | 8.8 | Boundary enclosures (fences/gates) | Item | 0 | 0 | 0 | 0 | 0 | Security fencing, gates, boundary walls, railings
8 | 8.9 | External lighting | Item | 0 | 0 | 0 | 0 | 0 | Column or wall-mounted lighting (see also 5.10)
WORKS COST SUBTOTAL (Groups 0–8) | [6 empty] | 218770.9 | 272849.1
ADDITIONS TO WORKS COST — Adjust % using signal rules in Notes column
Code |  |  | Description | Applied To | Low % | High % | Total LOW (£) | Total HIGH (£) | Signal Rules / Notes
A |  |  | Contractor's Preliminaries | Works Cost | 8% | 10% | 17501.672 | 27284.91 | 8%=clean/vacant/short prog ¦ +0.5% per: 6-18mo prog, partial occ, restricted access ¦ cap 10%
B |  |  | Contractor's Overheads & Profit | Works Cost | 8% | 12% | 17501.672 | 32741.892 | >£5M→8-9% ¦ £1-5M→9-10% ¦ <£1M→10-12% ¦ Lower end = cost priority; upper = D&B/speed
CONSTRUCTION COST SUBTOTAL (Works + Prelims + OH&P) | [6 empty] | 253774.244 | 332875.902
C |  |  | Professional Fees | Construction Cost | 5% | 15% | 12688.7122 | 49931.3853 | Stage 0-1→12-15% ¦ Stage 2→10-13% ¦ Stage 3→7-10% ¦ Stage 4→5-7% ¦ +1-2% M&E/struct/BREEAM
D |  |  | Dev & Project Costs | Construction Cost | 2% | 4% | 5075.4849 | 13315.0361 | Full planning→3-4% ¦ LBC also→4% ¦ Permitted dev→2% ¦ +0.5% if no surveys yet
E |  |  | Risk Allowance | Works Cost | 5% | 10% | 10938.545 | 27284.91 | Baseline 5% ¦ +2% no surveys ¦ +1.5% asbestos/contamination ¦ +1% structural concern ¦ +1% hard deadline ¦ cap 10%
H |  |  | Client Contingency [FIXED 5%] | Works Cost | 5% | 5% | 10938.545 | 13642.455 | FIXED at 5% — held by client, not released to contractor. Do not adjust.
F |  |  | Inflation Allowance | Works Cost | 2% | 12% | 4375.418 | 32741.892 | Component 1: tender delay (0-18mo=2-6%) + Component 2: construction mid-point (6-24mo=1-4%) ¦ cap 12%
TOTAL PROJECT COST (excl. VAT) | [6 empty] | 297790.9491 | 469791.5804
G |  |  | VAT — reference only, NOT in total | Project Total | 20% | 20% | 59558.1898 | 93958.3161 | Recoverability must be confirmed with client Finance team. New build may attract zero-rating.
Implied blended Works Cost rate — cross-check against BCIS benchmarks: |  |  |  | 437.5418 |  | 545.6982
⚠ DISCLAIMER: Indicative only — RIBA Stage 0–1 without measured quantities. Rates from Rates Reference Table, cross-referenced Q2 2026 market data. Must be reviewed by a Chartered QS before use in any business case or budget approval. LOW–HIGH range = mid-point ± 11% (default spread 22%). Update GIFA, BCIS factor and Spread as required.

## Rfb – Standard
NRM1 ESTIMATE — REFURB / FIT-OUT — STANDARD / CAT A–B
Spec level: Modified layout, new M&E distribution, Cat A/B office or teaching space finish. ¦ RIBA Stage 0–1 indicative only ¦ Base date Q2 2026
Project Type: | Refurb / Fit-Out |  | Spec Level: | Standard / Cat A–B |  | Region: | West Midlands
GIFA (m²) ▼ update: | 500 |  | BCIS Location Factor ▼: | 94% |  | Spread ±% ▼: | 22%
Grp | Sub | Element / Description | Unit | Mid-Point £/m² | Low £/m² | High £/m² | Total LOW (£) | Total HIGH (£) | Notes / Rate Driver
GROUP 0 — FACILITATING WORKS
0 | 0.1 | Toxic/hazardous material removal | Item | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | Asbestos; increase if confirmed present (refurb/demo only)
0 | 0.2 | Demolition & structural alterations | Item | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | Selective or full demolition; structural openings
0 | 0.3 | Contaminated land remediation | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Brownfield/contaminated; specialist quote needed
0 | 0.4 | Ground stabilisation | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Underpinning/piling if ground risk identified
GROUP 1 — SUBSTRUCTURE
1 | 1.1 | Standard foundations (strip/pad) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | New build only; included in Group 7 rate for extensions
1 | 1.2 | Specialist foundations (piled) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Poor ground conditions; trigger from GI report
1 | 1.3 | Lowest floor construction (slab) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Ground bearing or suspended; inc DPM and insulation
1 | 1.4 | Basement excavation & structure | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | High uncertainty; specialist estimate recommended
GROUP 2 — SUPERSTRUCTURE
2 | 2.1 | Structural frame | m² | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Steel/concrete/timber; new build or major extensions only
2 | 2.2 | Upper floors | m² | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | New build or added floors; inc topping and insulation
2 | 2.3 | Roof structure & covering | m² | 51.7 | 46.013 | 57.387 | 23006.5 | 28693.5 | New or replacement; inc insulation, waterproofing, rainwater
2 | 2.4 | Stairs & ramps | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | RC, steel or timber; accessibility ramps
2 | 2.5 | External walls & facade | m² | 56.4 | 50.196 | 62.604 | 25098 | 31302 | Masonry/cladding; refurb = overcladding or repair only
2 | 2.6 | Windows & external doors | m² | 122.2 | 108.758 | 135.642 | 54379 | 67821 | uPVC (low) to aluminium curtain wall (high)
2 | 2.7 | Internal walls & partitions | m² | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | Blockwork, drywall or glazed; do not double-count Grp 3
2 | 2.8 | Internal doors & ironmongery | Nr | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | Fire-rated at upper range; standard at lower
GROUP 3 — INTERNAL FINISHES ★ ALWAYS INCLUDED
3 | 3.1 | Wall finishes | m² | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | Emulsion (low) → specialist tiling/feature panelling (high)
3 | 3.2 | Floor finishes | m² | 51.7 | 46.013 | 57.387 | 23006.5 | 28693.5 | Vinyl/carpet (low) → stone/raised access floor (high)
3 | 3.3 | Ceiling finishes | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | Emulsion (low) → bespoke acoustic ceiling system (high)
GROUP 4 — FITTINGS, FURNISHINGS & EQUIPMENT
4 | 4.1 | General fittings & built-in joinery | Item | 28.2 | 25.098 | 31.302 | 12549 | 15651 | Reception desks, shelving, built-in furniture
4 | 4.2 | Sanitary fittings & toilet fit-out | Nr | 16.92 | 15.0588 | 18.7812 | 7529.4 | 9390.6 | WC packs; uplift for accessible/changing facilities
4 | 4.3 | Kitchen / break-out area | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Fitted units, worktops, appliances
4 | 4.4 | Specialist equipment (lab/AV/med) | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Laboratory, medical, AV; confirm with specialist
GROUP 5 — MECHANICAL & ELECTRICAL SERVICES ★ KEY ELEMENT
5 | 5.1 | Sanitary plumbing (1st & 2nd fix) | m² | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | HWS, cold water, drainage connections
5 | 5.2 | Heating & hot water (LTHW/heat pump) | m² | 47 | 41.83 | 52.17 | 20915 | 26085 | LTHW system or heat pump; include buffer vessel
5 | 5.3 | Ventilation & air handling | m² | 42.3 | 37.647 | 46.953 | 18823.5 | 23476.5 | MVHR/AHU; uplift for lab/healthcare extract (+50-100%)
5 | 5.4 | Air conditioning & cooling | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | VRF/splits; omit if not in scope
5 | 5.5 | Gas installation | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Omit if all-electric; confirm with utility
5 | 5.6 | Sprinkler / fire suppression | m² | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | >18m height or insurer requirement
5 | 5.7 | Electrical distribution & switchgear | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | LV panels, distribution boards, earthing, containment
5 | 5.8 | Electrical wiring (1st & 2nd fix) | m² | 37.6 | 33.464 | 41.736 | 16732 | 20868 | All power and lighting circuits; inc containment
5 | 5.9 | Emergency lighting & fire alarm | m² | 18.8 | 16.732 | 20.868 | 8366 | 10434 | L2 minimum; upgrade for multi-zone/complex layouts
5 | 5.10 | External lighting | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Column/wall-mounted perimeter lighting
5 | 5.11 | Solar PV / renewables | kWp | 752 | 669.28 | 834.72 | 334640 | 417360 | £/kWp installed; coordinate structural loading + electrical
5 | 5.12 | EV charging points | Nr | 1410 | 1254.9 | 1565.1 | 627450 | 782550 | Per charge point inc groundworks; 7kW fast charger
5 | 5.13 | IT / data infrastructure (Cat6A) | m² | 16.92 | 15.0588 | 18.7812 | 7529.4 | 9390.6 | Cabling, containment, patch panels
5 | 5.14 | AV systems | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Lecture rooms, boardrooms; specialist-designed
5 | 5.15 | Access control & CCTV / security | m² | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Door access readers, CCTV; varies by security level
5 | 5.16 | Lifts & platform lifts | Nr | 75.2 | 66.928 | 83.472 | 33464 | 41736 | Per installation × Nr; inc shaft if new build
5 | 5.17 | Builder's work in connection (BWIC) | m² | 11.28 | 10.0392 | 12.5208 | 5019.6 | 6260.4 | Penetrations, plinths, ducts, concrete bases for plant
GROUP 6 — PREFABRICATED / MODULAR (if applicable)
6 | 6.1 | Prefabricated / modular units | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Factory-built modular; specialist quote required
6 | 6.2 | Pre-engineered systems (mezzanine) | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Mezzanine floors, demountable partitions
GROUP 7 — WORK TO EXISTING BUILDINGS
7 | 7.1 | Structural repairs | Item | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | Crack stitching, bearing repairs; increase for poor condition
7 | 7.2 | Fabric / envelope repairs | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Repointing, waterproofing, weathertight works
7 | 7.3 | Damp proof course treatment | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Chemical DPC; increase for severe rising damp
7 | 7.4 | M&E overhaul / life-expired services | Item | 28.2 | 25.098 | 31.302 | 12549 | 15651 | Replacement of end-of-life mechanical & electrical plant
7 | 7.5 | Making good after structural works | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Patch plaster, redecoration after structural alterations
GROUP 8 — EXTERNAL WORKS
8 | 8.1 | Site preparation & clearance | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Strip topsoil, vegetation, temp fencing and hoarding
8 | 8.2 | Roads, paths & hard paving | m² | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Macadam/block paving; inc edging and drainage channels
8 | 8.3 | Car parking (line-marked bays) | Nr | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Surfacing, line markings, disabled bays
8 | 8.4 | Surface water drainage | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Gullies, pipes, SuDS if required by planning
8 | 8.5 | Foul drainage connections | Item | 5.64 | 5.0196 | 6.2604 | 2509.8 | 3130.2 | Connection to existing drain or new manhole
8 | 8.6 | External utility services | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Gas/water/electric diversions; early check with DNO
8 | 8.7 | Soft landscaping | m² | 2.82 | 2.5098 | 3.1302 | 1254.9 | 1565.1 | Planting, seeding, topsoil reinstatement
8 | 8.8 | Boundary enclosures (fences/gates) | Item | 2.82 | 2.5098 | 3.1302 | 1254.9 | 1565.1 | Security fencing, gates, boundary walls, railings
8 | 8.9 | External lighting | Item | 1.88 | 1.6732 | 2.0868 | 836.6 | 1043.4 | Column or wall-mounted lighting (see also 5.10)
WORKS COST SUBTOTAL (Groups 0–8) | [6 empty] | 1459448.7 | 1820211.3
ADDITIONS TO WORKS COST — Adjust % using signal rules in Notes column
Code |  |  | Description | Applied To | Low % | High % | Total LOW (£) | Total HIGH (£) | Signal Rules / Notes
A |  |  | Contractor's Preliminaries | Works Cost | 8% | 10% | 116755.896 | 182021.13 | 8%=clean/vacant/short prog ¦ +0.5% per: 6-18mo prog, partial occ, restricted access ¦ cap 10%
B |  |  | Contractor's Overheads & Profit | Works Cost | 8% | 12% | 116755.896 | 218425.356 | >£5M→8-9% ¦ £1-5M→9-10% ¦ <£1M→10-12% ¦ Lower end = cost priority; upper = D&B/speed
CONSTRUCTION COST SUBTOTAL (Works + Prelims + OH&P) | [6 empty] | 1692960.492 | 2220657.786
C |  |  | Professional Fees | Construction Cost | 5% | 15% | 84648.0246 | 333098.6679 | Stage 0-1→12-15% ¦ Stage 2→10-13% ¦ Stage 3→7-10% ¦ Stage 4→5-7% ¦ +1-2% M&E/struct/BREEAM
D |  |  | Dev & Project Costs | Construction Cost | 2% | 4% | 33859.2098 | 88826.3114 | Full planning→3-4% ¦ LBC also→4% ¦ Permitted dev→2% ¦ +0.5% if no surveys yet
E |  |  | Risk Allowance | Works Cost | 5% | 10% | 72972.435 | 182021.13 | Baseline 5% ¦ +2% no surveys ¦ +1.5% asbestos/contamination ¦ +1% structural concern ¦ +1% hard deadline ¦ cap 10%
H |  |  | Client Contingency [FIXED 5%] | Works Cost | 5% | 5% | 72972.435 | 91010.565 | FIXED at 5% — held by client, not released to contractor. Do not adjust.
F |  |  | Inflation Allowance | Works Cost | 2% | 12% | 29188.974 | 218425.356 | Component 1: tender delay (0-18mo=2-6%) + Component 2: construction mid-point (6-24mo=1-4%) ¦ cap 12%
TOTAL PROJECT COST (excl. VAT) | [6 empty] | 1986601.5704 | 3134039.8163
G |  |  | VAT — reference only, NOT in total | Project Total | 20% | 20% | 397320.3141 | 626807.9633 | Recoverability must be confirmed with client Finance team. New build may attract zero-rating.
Implied blended Works Cost rate — cross-check against BCIS benchmarks: |  |  |  | 2918.8974 |  | 3640.4226
⚠ DISCLAIMER: Indicative only — RIBA Stage 0–1 without measured quantities. Rates from Rates Reference Table, cross-referenced Q2 2026 market data. Must be reviewed by a Chartered QS before use in any business case or budget approval. LOW–HIGH range = mid-point ± 11% (default spread 22%). Update GIFA, BCIS factor and Spread as required.

## Rfb – High Spec
NRM1 ESTIMATE — REFURB / FIT-OUT — HIGH SPEC / SPECIALIST
Spec level: Flagship, lab, healthcare or bespoke. Heavy M&E, specialist fit-out, feature finishes. ¦ RIBA Stage 0–1 indicative only ¦ Base date Q2 2026
Project Type: | Refurb / Fit-Out |  | Spec Level: | High Spec / Specialist |  | Region: | West Midlands
GIFA (m²) ▼ update: | 500 |  | BCIS Location Factor ▼: | 94% |  | Spread ±% ▼: | 22%
Grp | Sub | Element / Description | Unit | Mid-Point £/m² | Low £/m² | High £/m² | Total LOW (£) | Total HIGH (£) | Notes / Rate Driver
GROUP 0 — FACILITATING WORKS
0 | 0.1 | Toxic/hazardous material removal | Item | 37.6 | 33.464 | 41.736 | 16732 | 20868 | Asbestos; increase if confirmed present (refurb/demo only)
0 | 0.2 | Demolition & structural alterations | Item | 51.7 | 46.013 | 57.387 | 23006.5 | 28693.5 | Selective or full demolition; structural openings
0 | 0.3 | Contaminated land remediation | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Brownfield/contaminated; specialist quote needed
0 | 0.4 | Ground stabilisation | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Underpinning/piling if ground risk identified
GROUP 1 — SUBSTRUCTURE
1 | 1.1 | Standard foundations (strip/pad) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | New build only; included in Group 7 rate for extensions
1 | 1.2 | Specialist foundations (piled) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Poor ground conditions; trigger from GI report
1 | 1.3 | Lowest floor construction (slab) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Ground bearing or suspended; inc DPM and insulation
1 | 1.4 | Basement excavation & structure | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | High uncertainty; specialist estimate recommended
GROUP 2 — SUPERSTRUCTURE
2 | 2.1 | Structural frame | m² | 37.6 | 33.464 | 41.736 | 16732 | 20868 | Steel/concrete/timber; new build or major extensions only
2 | 2.2 | Upper floors | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | New build or added floors; inc topping and insulation
2 | 2.3 | Roof structure & covering | m² | 84.6 | 75.294 | 93.906 | 37647 | 46953 | New or replacement; inc insulation, waterproofing, rainwater
2 | 2.4 | Stairs & ramps | Item | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | RC, steel or timber; accessibility ramps
2 | 2.5 | External walls & facade | m² | 103.4 | 92.026 | 114.774 | 46013 | 57387 | Masonry/cladding; refurb = overcladding or repair only
2 | 2.6 | Windows & external doors | m² | 188 | 167.32 | 208.68 | 83660 | 104340 | uPVC (low) to aluminium curtain wall (high)
2 | 2.7 | Internal walls & partitions | m² | 56.4 | 50.196 | 62.604 | 25098 | 31302 | Blockwork, drywall or glazed; do not double-count Grp 3
2 | 2.8 | Internal doors & ironmongery | Nr | 37.6 | 33.464 | 41.736 | 16732 | 20868 | Fire-rated at upper range; standard at lower
GROUP 3 — INTERNAL FINISHES ★ ALWAYS INCLUDED
3 | 3.1 | Wall finishes | m² | 70.5 | 62.745 | 78.255 | 31372.5 | 39127.5 | Emulsion (low) → specialist tiling/feature panelling (high)
3 | 3.2 | Floor finishes | m² | 122.2 | 108.758 | 135.642 | 54379 | 67821 | Vinyl/carpet (low) → stone/raised access floor (high)
3 | 3.3 | Ceiling finishes | m² | 61.1 | 54.379 | 67.821 | 27189.5 | 33910.5 | Emulsion (low) → bespoke acoustic ceiling system (high)
GROUP 4 — FITTINGS, FURNISHINGS & EQUIPMENT
4 | 4.1 | General fittings & built-in joinery | Item | 75.2 | 66.928 | 83.472 | 33464 | 41736 | Reception desks, shelving, built-in furniture
4 | 4.2 | Sanitary fittings & toilet fit-out | Nr | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | WC packs; uplift for accessible/changing facilities
4 | 4.3 | Kitchen / break-out area | Item | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | Fitted units, worktops, appliances
4 | 4.4 | Specialist equipment (lab/AV/med) | Item | 75.2 | 66.928 | 83.472 | 33464 | 41736 | Laboratory, medical, AV; confirm with specialist
GROUP 5 — MECHANICAL & ELECTRICAL SERVICES ★ KEY ELEMENT
5 | 5.1 | Sanitary plumbing (1st & 2nd fix) | m² | 61.1 | 54.379 | 67.821 | 27189.5 | 33910.5 | HWS, cold water, drainage connections
5 | 5.2 | Heating & hot water (LTHW/heat pump) | m² | 84.6 | 75.294 | 93.906 | 37647 | 46953 | LTHW system or heat pump; include buffer vessel
5 | 5.3 | Ventilation & air handling | m² | 84.6 | 75.294 | 93.906 | 37647 | 46953 | MVHR/AHU; uplift for lab/healthcare extract (+50-100%)
5 | 5.4 | Air conditioning & cooling | m² | 65.8 | 58.562 | 73.038 | 29281 | 36519 | VRF/splits; omit if not in scope
5 | 5.5 | Gas installation | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Omit if all-electric; confirm with utility
5 | 5.6 | Sprinkler / fire suppression | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | >18m height or insurer requirement
5 | 5.7 | Electrical distribution & switchgear | m² | 51.7 | 46.013 | 57.387 | 23006.5 | 28693.5 | LV panels, distribution boards, earthing, containment
5 | 5.8 | Electrical wiring (1st & 2nd fix) | m² | 70.5 | 62.745 | 78.255 | 31372.5 | 39127.5 | All power and lighting circuits; inc containment
5 | 5.9 | Emergency lighting & fire alarm | m² | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | L2 minimum; upgrade for multi-zone/complex layouts
5 | 5.10 | External lighting | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Column/wall-mounted perimeter lighting
5 | 5.11 | Solar PV / renewables | kWp | 1128 | 1003.92 | 1252.08 | 501960 | 626040 | £/kWp installed; coordinate structural loading + electrical
5 | 5.12 | EV charging points | Nr | 2350 | 2091.5 | 2608.5 | 1045750 | 1304250 | Per charge point inc groundworks; 7kW fast charger
5 | 5.13 | IT / data infrastructure (Cat6A) | m² | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | Cabling, containment, patch panels
5 | 5.14 | AV systems | Item | 47 | 41.83 | 52.17 | 20915 | 26085 | Lecture rooms, boardrooms; specialist-designed
5 | 5.15 | Access control & CCTV / security | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | Door access readers, CCTV; varies by security level
5 | 5.16 | Lifts & platform lifts | Nr | 112.8 | 100.392 | 125.208 | 50196 | 62604 | Per installation × Nr; inc shaft if new build
5 | 5.17 | Builder's work in connection (BWIC) | m² | 20.68 | 18.4052 | 22.9548 | 9202.6 | 11477.4 | Penetrations, plinths, ducts, concrete bases for plant
GROUP 6 — PREFABRICATED / MODULAR (if applicable)
6 | 6.1 | Prefabricated / modular units | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Factory-built modular; specialist quote required
6 | 6.2 | Pre-engineered systems (mezzanine) | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Mezzanine floors, demountable partitions
GROUP 7 — WORK TO EXISTING BUILDINGS
7 | 7.1 | Structural repairs | Item | 51.7 | 46.013 | 57.387 | 23006.5 | 28693.5 | Crack stitching, bearing repairs; increase for poor condition
7 | 7.2 | Fabric / envelope repairs | Item | 42.3 | 37.647 | 46.953 | 18823.5 | 23476.5 | Repointing, waterproofing, weathertight works
7 | 7.3 | Damp proof course treatment | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Chemical DPC; increase for severe rising damp
7 | 7.4 | M&E overhaul / life-expired services | Item | 75.2 | 66.928 | 83.472 | 33464 | 41736 | Replacement of end-of-life mechanical & electrical plant
7 | 7.5 | Making good after structural works | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Patch plaster, redecoration after structural alterations
GROUP 8 — EXTERNAL WORKS
8 | 8.1 | Site preparation & clearance | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Strip topsoil, vegetation, temp fencing and hoarding
8 | 8.2 | Roads, paths & hard paving | m² | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Macadam/block paving; inc edging and drainage channels
8 | 8.3 | Car parking (line-marked bays) | Nr | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Surfacing, line markings, disabled bays
8 | 8.4 | Surface water drainage | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Gullies, pipes, SuDS if required by planning
8 | 8.5 | Foul drainage connections | Item | 11.28 | 10.0392 | 12.5208 | 5019.6 | 6260.4 | Connection to existing drain or new manhole
8 | 8.6 | External utility services | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Gas/water/electric diversions; early check with DNO
8 | 8.7 | Soft landscaping | m² | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Planting, seeding, topsoil reinstatement
8 | 8.8 | Boundary enclosures (fences/gates) | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Security fencing, gates, boundary walls, railings
8 | 8.9 | External lighting | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Column or wall-mounted lighting (see also 5.10)
WORKS COST SUBTOTAL (Groups 0–8) | [6 empty] | 2528623.5 | 3153676.5
ADDITIONS TO WORKS COST — Adjust % using signal rules in Notes column
Code |  |  | Description | Applied To | Low % | High % | Total LOW (£) | Total HIGH (£) | Signal Rules / Notes
A |  |  | Contractor's Preliminaries | Works Cost | 8% | 10% | 202289.88 | 315367.65 | 8%=clean/vacant/short prog ¦ +0.5% per: 6-18mo prog, partial occ, restricted access ¦ cap 10%
B |  |  | Contractor's Overheads & Profit | Works Cost | 8% | 12% | 202289.88 | 378441.18 | >£5M→8-9% ¦ £1-5M→9-10% ¦ <£1M→10-12% ¦ Lower end = cost priority; upper = D&B/speed
CONSTRUCTION COST SUBTOTAL (Works + Prelims + OH&P) | [6 empty] | 2933203.26 | 3847485.33
C |  |  | Professional Fees | Construction Cost | 5% | 15% | 146660.163 | 577122.7995 | Stage 0-1→12-15% ¦ Stage 2→10-13% ¦ Stage 3→7-10% ¦ Stage 4→5-7% ¦ +1-2% M&E/struct/BREEAM
D |  |  | Dev & Project Costs | Construction Cost | 2% | 4% | 58664.0652 | 153899.4132 | Full planning→3-4% ¦ LBC also→4% ¦ Permitted dev→2% ¦ +0.5% if no surveys yet
E |  |  | Risk Allowance | Works Cost | 5% | 10% | 126431.175 | 315367.65 | Baseline 5% ¦ +2% no surveys ¦ +1.5% asbestos/contamination ¦ +1% structural concern ¦ +1% hard deadline ¦ cap 10%
H |  |  | Client Contingency [FIXED 5%] | Works Cost | 5% | 5% | 126431.175 | 157683.825 | FIXED at 5% — held by client, not released to contractor. Do not adjust.
F |  |  | Inflation Allowance | Works Cost | 2% | 12% | 50572.47 | 378441.18 | Component 1: tender delay (0-18mo=2-6%) + Component 2: construction mid-point (6-24mo=1-4%) ¦ cap 12%
TOTAL PROJECT COST (excl. VAT) | [6 empty] | 3441962.3082 | 5430000.1977
G |  |  | VAT — reference only, NOT in total | Project Total | 20% | 20% | 688392.4616 | 1086000.0395 | Recoverability must be confirmed with client Finance team. New build may attract zero-rating.
Implied blended Works Cost rate — cross-check against BCIS benchmarks: |  |  |  | 5057.247 |  | 6307.353
⚠ DISCLAIMER: Indicative only — RIBA Stage 0–1 without measured quantities. Rates from Rates Reference Table, cross-referenced Q2 2026 market data. Must be reviewed by a Chartered QS before use in any business case or budget approval. LOW–HIGH range = mid-point ± 11% (default spread 22%). Update GIFA, BCIS factor and Spread as required.

## NB – Standard
NRM1 ESTIMATE — NEW BUILD — STANDARD
Spec level: Standard commercial/education new build. Conventional construction, standard M&E. ¦ RIBA Stage 0–1 indicative only ¦ Base date Q2 2026
Project Type: | New Build |  | Spec Level: | Standard |  | Region: | West Midlands
GIFA (m²) ▼ update: | 500 |  | BCIS Location Factor ▼: | 94% |  | Spread ±% ▼: | 22%
Grp | Sub | Element / Description | Unit | Mid-Point £/m² | Low £/m² | High £/m² | Total LOW (£) | Total HIGH (£) | Notes / Rate Driver
GROUP 0 — FACILITATING WORKS
0 | 0.1 | Toxic/hazardous material removal | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Asbestos; increase if confirmed present (refurb/demo only)
0 | 0.2 | Demolition & structural alterations | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Selective or full demolition; structural openings
0 | 0.3 | Contaminated land remediation | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Brownfield/contaminated; specialist quote needed
0 | 0.4 | Ground stabilisation | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Underpinning/piling if ground risk identified
GROUP 1 — SUBSTRUCTURE
1 | 1.1 | Standard foundations (strip/pad) | m² | 51.7 | 46.013 | 57.387 | 23006.5 | 28693.5 | New build only; included in Group 7 rate for extensions
1 | 1.2 | Specialist foundations (piled) | m² | 37.6 | 33.464 | 41.736 | 16732 | 20868 | Poor ground conditions; trigger from GI report
1 | 1.3 | Lowest floor construction (slab) | m² | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | Ground bearing or suspended; inc DPM and insulation
1 | 1.4 | Basement excavation & structure | Item | 75.2 | 66.928 | 83.472 | 33464 | 41736 | High uncertainty; specialist estimate recommended
GROUP 2 — SUPERSTRUCTURE
2 | 2.1 | Structural frame | m² | 141 | 125.49 | 156.51 | 62745 | 78255 | Steel/concrete/timber; new build or major extensions only
2 | 2.2 | Upper floors | m² | 61.1 | 54.379 | 67.821 | 27189.5 | 33910.5 | New build or added floors; inc topping and insulation
2 | 2.3 | Roof structure & covering | m² | 70.5 | 62.745 | 78.255 | 31372.5 | 39127.5 | New or replacement; inc insulation, waterproofing, rainwater
2 | 2.4 | Stairs & ramps | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | RC, steel or timber; accessibility ramps
2 | 2.5 | External walls & facade | m² | 188 | 167.32 | 208.68 | 83660 | 104340 | Masonry/cladding; refurb = overcladding or repair only
2 | 2.6 | Windows & external doors | m² | 94 | 83.66 | 104.34 | 41830 | 52170 | uPVC (low) to aluminium curtain wall (high)
2 | 2.7 | Internal walls & partitions | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | Blockwork, drywall or glazed; do not double-count Grp 3
2 | 2.8 | Internal doors & ironmongery | Nr | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Fire-rated at upper range; standard at lower
GROUP 3 — INTERNAL FINISHES ★ ALWAYS INCLUDED
3 | 3.1 | Wall finishes | m² | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | Emulsion (low) → specialist tiling/feature panelling (high)
3 | 3.2 | Floor finishes | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | Vinyl/carpet (low) → stone/raised access floor (high)
3 | 3.3 | Ceiling finishes | m² | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Emulsion (low) → bespoke acoustic ceiling system (high)
GROUP 4 — FITTINGS, FURNISHINGS & EQUIPMENT
4 | 4.1 | General fittings & built-in joinery | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Reception desks, shelving, built-in furniture
4 | 4.2 | Sanitary fittings & toilet fit-out | Nr | 9.4 | 8.366 | 10.434 | 4183 | 5217 | WC packs; uplift for accessible/changing facilities
4 | 4.3 | Kitchen / break-out area | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Fitted units, worktops, appliances
4 | 4.4 | Specialist equipment (lab/AV/med) | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Laboratory, medical, AV; confirm with specialist
GROUP 5 — MECHANICAL & ELECTRICAL SERVICES ★ KEY ELEMENT
5 | 5.1 | Sanitary plumbing (1st & 2nd fix) | m² | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | HWS, cold water, drainage connections
5 | 5.2 | Heating & hot water (LTHW/heat pump) | m² | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | LTHW system or heat pump; include buffer vessel
5 | 5.3 | Ventilation & air handling | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | MVHR/AHU; uplift for lab/healthcare extract (+50-100%)
5 | 5.4 | Air conditioning & cooling | m² | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | VRF/splits; omit if not in scope
5 | 5.5 | Gas installation | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Omit if all-electric; confirm with utility
5 | 5.6 | Sprinkler / fire suppression | m² | 9.4 | 8.366 | 10.434 | 4183 | 5217 | >18m height or insurer requirement
5 | 5.7 | Electrical distribution & switchgear | m² | 18.8 | 16.732 | 20.868 | 8366 | 10434 | LV panels, distribution boards, earthing, containment
5 | 5.8 | Electrical wiring (1st & 2nd fix) | m² | 28.2 | 25.098 | 31.302 | 12549 | 15651 | All power and lighting circuits; inc containment
5 | 5.9 | Emergency lighting & fire alarm | m² | 11.28 | 10.0392 | 12.5208 | 5019.6 | 6260.4 | L2 minimum; upgrade for multi-zone/complex layouts
5 | 5.10 | External lighting | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Column/wall-mounted perimeter lighting
5 | 5.11 | Solar PV / renewables | kWp | 752 | 669.28 | 834.72 | 334640 | 417360 | £/kWp installed; coordinate structural loading + electrical
5 | 5.12 | EV charging points | Nr | 1410 | 1254.9 | 1565.1 | 627450 | 782550 | Per charge point inc groundworks; 7kW fast charger
5 | 5.13 | IT / data infrastructure (Cat6A) | m² | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Cabling, containment, patch panels
5 | 5.14 | AV systems | Item | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Lecture rooms, boardrooms; specialist-designed
5 | 5.15 | Access control & CCTV / security | m² | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Door access readers, CCTV; varies by security level
5 | 5.16 | Lifts & platform lifts | Nr | 56.4 | 50.196 | 62.604 | 25098 | 31302 | Per installation × Nr; inc shaft if new build
5 | 5.17 | Builder's work in connection (BWIC) | m² | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Penetrations, plinths, ducts, concrete bases for plant
GROUP 6 — PREFABRICATED / MODULAR (if applicable)
6 | 6.1 | Prefabricated / modular units | Item | 0 | 0 | 0 | 0 | 0 | Factory-built modular; specialist quote required
6 | 6.2 | Pre-engineered systems (mezzanine) | Item | 0 | 0 | 0 | 0 | 0 | Mezzanine floors, demountable partitions
GROUP 7 — WORK TO EXISTING BUILDINGS
7 | 7.1 | Structural repairs | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Crack stitching, bearing repairs; increase for poor condition
7 | 7.2 | Fabric / envelope repairs | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Repointing, waterproofing, weathertight works
7 | 7.3 | Damp proof course treatment | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Chemical DPC; increase for severe rising damp
7 | 7.4 | M&E overhaul / life-expired services | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Replacement of end-of-life mechanical & electrical plant
7 | 7.5 | Making good after structural works | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Patch plaster, redecoration after structural alterations
GROUP 8 — EXTERNAL WORKS
8 | 8.1 | Site preparation & clearance | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Strip topsoil, vegetation, temp fencing and hoarding
8 | 8.2 | Roads, paths & hard paving | m² | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Macadam/block paving; inc edging and drainage channels
8 | 8.3 | Car parking (line-marked bays) | Nr | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Surfacing, line markings, disabled bays
8 | 8.4 | Surface water drainage | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Gullies, pipes, SuDS if required by planning
8 | 8.5 | Foul drainage connections | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Connection to existing drain or new manhole
8 | 8.6 | External utility services | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Gas/water/electric diversions; early check with DNO
8 | 8.7 | Soft landscaping | m² | 4.7 | 4.183 | 5.217 | 2091.5 | 2608.5 | Planting, seeding, topsoil reinstatement
8 | 8.8 | Boundary enclosures (fences/gates) | Item | 2.82 | 2.5098 | 3.1302 | 1254.9 | 1565.1 | Security fencing, gates, boundary walls, railings
8 | 8.9 | External lighting | Item | 2.82 | 2.5098 | 3.1302 | 1254.9 | 1565.1 | Column or wall-mounted lighting (see also 5.10)
WORKS COST SUBTOTAL (Groups 0–8) | [6 empty] | 1534742.7 | 1914117.3
ADDITIONS TO WORKS COST — Adjust % using signal rules in Notes column
Code |  |  | Description | Applied To | Low % | High % | Total LOW (£) | Total HIGH (£) | Signal Rules / Notes
A |  |  | Contractor's Preliminaries | Works Cost | 8% | 10% | 122779.416 | 191411.73 | 8%=clean/vacant/short prog ¦ +0.5% per: 6-18mo prog, partial occ, restricted access ¦ cap 10%
B |  |  | Contractor's Overheads & Profit | Works Cost | 8% | 12% | 122779.416 | 229694.076 | >£5M→8-9% ¦ £1-5M→9-10% ¦ <£1M→10-12% ¦ Lower end = cost priority; upper = D&B/speed
CONSTRUCTION COST SUBTOTAL (Works + Prelims + OH&P) | [6 empty] | 1780301.532 | 2335223.106
C |  |  | Professional Fees | Construction Cost | 5% | 15% | 89015.0766 | 350283.4659 | Stage 0-1→12-15% ¦ Stage 2→10-13% ¦ Stage 3→7-10% ¦ Stage 4→5-7% ¦ +1-2% M&E/struct/BREEAM
D |  |  | Dev & Project Costs | Construction Cost | 2% | 4% | 35606.0306 | 93408.9242 | Full planning→3-4% ¦ LBC also→4% ¦ Permitted dev→2% ¦ +0.5% if no surveys yet
E |  |  | Risk Allowance | Works Cost | 5% | 10% | 76737.135 | 191411.73 | Baseline 5% ¦ +2% no surveys ¦ +1.5% asbestos/contamination ¦ +1% structural concern ¦ +1% hard deadline ¦ cap 10%
H |  |  | Client Contingency [FIXED 5%] | Works Cost | 5% | 5% | 76737.135 | 95705.865 | FIXED at 5% — held by client, not released to contractor. Do not adjust.
F |  |  | Inflation Allowance | Works Cost | 2% | 12% | 30694.854 | 229694.076 | Component 1: tender delay (0-18mo=2-6%) + Component 2: construction mid-point (6-24mo=1-4%) ¦ cap 12%
TOTAL PROJECT COST (excl. VAT) | [6 empty] | 2089091.7632 | 3295727.1671
G |  |  | VAT — reference only, NOT in total | Project Total | 20% | 20% | 417818.3526 | 659145.4334 | Recoverability must be confirmed with client Finance team. New build may attract zero-rating.
Implied blended Works Cost rate — cross-check against BCIS benchmarks: |  |  |  | 3069.4854 |  | 3828.2346
⚠ DISCLAIMER: Indicative only — RIBA Stage 0–1 without measured quantities. Rates from Rates Reference Table, cross-referenced Q2 2026 market data. Must be reviewed by a Chartered QS before use in any business case or budget approval. LOW–HIGH range = mid-point ± 11% (default spread 22%). Update GIFA, BCIS factor and Spread as required.

## NB – High Spec
NRM1 ESTIMATE — NEW BUILD — HIGH SPEC / SPECIALIST
Spec level: High specification new build — lab, healthcare, flagship or technically complex. ¦ RIBA Stage 0–1 indicative only ¦ Base date Q2 2026
Project Type: | New Build |  | Spec Level: | High Spec / Specialist |  | Region: | West Midlands
GIFA (m²) ▼ update: | 500 |  | BCIS Location Factor ▼: | 94% |  | Spread ±% ▼: | 22%
Grp | Sub | Element / Description | Unit | Mid-Point £/m² | Low £/m² | High £/m² | Total LOW (£) | Total HIGH (£) | Notes / Rate Driver
GROUP 0 — FACILITATING WORKS
0 | 0.1 | Toxic/hazardous material removal | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Asbestos; increase if confirmed present (refurb/demo only)
0 | 0.2 | Demolition & structural alterations | Item | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | Selective or full demolition; structural openings
0 | 0.3 | Contaminated land remediation | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Brownfield/contaminated; specialist quote needed
0 | 0.4 | Ground stabilisation | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Underpinning/piling if ground risk identified
GROUP 1 — SUBSTRUCTURE
1 | 1.1 | Standard foundations (strip/pad) | m² | 75.2 | 66.928 | 83.472 | 33464 | 41736 | New build only; included in Group 7 rate for extensions
1 | 1.2 | Specialist foundations (piled) | m² | 56.4 | 50.196 | 62.604 | 25098 | 31302 | Poor ground conditions; trigger from GI report
1 | 1.3 | Lowest floor construction (slab) | m² | 51.7 | 46.013 | 57.387 | 23006.5 | 28693.5 | Ground bearing or suspended; inc DPM and insulation
1 | 1.4 | Basement excavation & structure | Item | 141 | 125.49 | 156.51 | 62745 | 78255 | High uncertainty; specialist estimate recommended
GROUP 2 — SUPERSTRUCTURE
2 | 2.1 | Structural frame | m² | 206.8 | 184.052 | 229.548 | 92026 | 114774 | Steel/concrete/timber; new build or major extensions only
2 | 2.2 | Upper floors | m² | 89.3 | 79.477 | 99.123 | 39738.5 | 49561.5 | New build or added floors; inc topping and insulation
2 | 2.3 | Roof structure & covering | m² | 112.8 | 100.392 | 125.208 | 50196 | 62604 | New or replacement; inc insulation, waterproofing, rainwater
2 | 2.4 | Stairs & ramps | Item | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | RC, steel or timber; accessibility ramps
2 | 2.5 | External walls & facade | m² | 300.8 | 267.712 | 333.888 | 133856 | 166944 | Masonry/cladding; refurb = overcladding or repair only
2 | 2.6 | Windows & external doors | m² | 150.4 | 133.856 | 166.944 | 66928 | 83472 | uPVC (low) to aluminium curtain wall (high)
2 | 2.7 | Internal walls & partitions | m² | 47 | 41.83 | 52.17 | 20915 | 26085 | Blockwork, drywall or glazed; do not double-count Grp 3
2 | 2.8 | Internal doors & ironmongery | Nr | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | Fire-rated at upper range; standard at lower
GROUP 3 — INTERNAL FINISHES ★ ALWAYS INCLUDED
3 | 3.1 | Wall finishes | m² | 51.7 | 46.013 | 57.387 | 23006.5 | 28693.5 | Emulsion (low) → specialist tiling/feature panelling (high)
3 | 3.2 | Floor finishes | m² | 75.2 | 66.928 | 83.472 | 33464 | 41736 | Vinyl/carpet (low) → stone/raised access floor (high)
3 | 3.3 | Ceiling finishes | m² | 42.3 | 37.647 | 46.953 | 18823.5 | 23476.5 | Emulsion (low) → bespoke acoustic ceiling system (high)
GROUP 4 — FITTINGS, FURNISHINGS & EQUIPMENT
4 | 4.1 | General fittings & built-in joinery | Item | 47 | 41.83 | 52.17 | 20915 | 26085 | Reception desks, shelving, built-in furniture
4 | 4.2 | Sanitary fittings & toilet fit-out | Nr | 20.68 | 18.4052 | 22.9548 | 9202.6 | 11477.4 | WC packs; uplift for accessible/changing facilities
4 | 4.3 | Kitchen / break-out area | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Fitted units, worktops, appliances
4 | 4.4 | Specialist equipment (lab/AV/med) | Item | 56.4 | 50.196 | 62.604 | 25098 | 31302 | Laboratory, medical, AV; confirm with specialist
GROUP 5 — MECHANICAL & ELECTRICAL SERVICES ★ KEY ELEMENT
5 | 5.1 | Sanitary plumbing (1st & 2nd fix) | m² | 47 | 41.83 | 52.17 | 20915 | 26085 | HWS, cold water, drainage connections
5 | 5.2 | Heating & hot water (LTHW/heat pump) | m² | 65.8 | 58.562 | 73.038 | 29281 | 36519 | LTHW system or heat pump; include buffer vessel
5 | 5.3 | Ventilation & air handling | m² | 65.8 | 58.562 | 73.038 | 29281 | 36519 | MVHR/AHU; uplift for lab/healthcare extract (+50-100%)
5 | 5.4 | Air conditioning & cooling | m² | 51.7 | 46.013 | 57.387 | 23006.5 | 28693.5 | VRF/splits; omit if not in scope
5 | 5.5 | Gas installation | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Omit if all-electric; confirm with utility
5 | 5.6 | Sprinkler / fire suppression | m² | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | >18m height or insurer requirement
5 | 5.7 | Electrical distribution & switchgear | m² | 42.3 | 37.647 | 46.953 | 18823.5 | 23476.5 | LV panels, distribution boards, earthing, containment
5 | 5.8 | Electrical wiring (1st & 2nd fix) | m² | 56.4 | 50.196 | 62.604 | 25098 | 31302 | All power and lighting circuits; inc containment
5 | 5.9 | Emergency lighting & fire alarm | m² | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | L2 minimum; upgrade for multi-zone/complex layouts
5 | 5.10 | External lighting | Item | 11.28 | 10.0392 | 12.5208 | 5019.6 | 6260.4 | Column/wall-mounted perimeter lighting
5 | 5.11 | Solar PV / renewables | kWp | 1128 | 1003.92 | 1252.08 | 501960 | 626040 | £/kWp installed; coordinate structural loading + electrical
5 | 5.12 | EV charging points | Nr | 2350 | 2091.5 | 2608.5 | 1045750 | 1304250 | Per charge point inc groundworks; 7kW fast charger
5 | 5.13 | IT / data infrastructure (Cat6A) | m² | 23.5 | 20.915 | 26.085 | 10457.5 | 13042.5 | Cabling, containment, patch panels
5 | 5.14 | AV systems | Item | 37.6 | 33.464 | 41.736 | 16732 | 20868 | Lecture rooms, boardrooms; specialist-designed
5 | 5.15 | Access control & CCTV / security | m² | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Door access readers, CCTV; varies by security level
5 | 5.16 | Lifts & platform lifts | Nr | 94 | 83.66 | 104.34 | 41830 | 52170 | Per installation × Nr; inc shaft if new build
5 | 5.17 | Builder's work in connection (BWIC) | m² | 16.92 | 15.0588 | 18.7812 | 7529.4 | 9390.6 | Penetrations, plinths, ducts, concrete bases for plant
GROUP 6 — PREFABRICATED / MODULAR (if applicable)
6 | 6.1 | Prefabricated / modular units | Item | 141 | 125.49 | 156.51 | 62745 | 78255 | Factory-built modular; specialist quote required
6 | 6.2 | Pre-engineered systems (mezzanine) | Item | 75.2 | 66.928 | 83.472 | 33464 | 41736 | Mezzanine floors, demountable partitions
GROUP 7 — WORK TO EXISTING BUILDINGS
7 | 7.1 | Structural repairs | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Crack stitching, bearing repairs; increase for poor condition
7 | 7.2 | Fabric / envelope repairs | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Repointing, waterproofing, weathertight works
7 | 7.3 | Damp proof course treatment | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Chemical DPC; increase for severe rising damp
7 | 7.4 | M&E overhaul / life-expired services | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Replacement of end-of-life mechanical & electrical plant
7 | 7.5 | Making good after structural works | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Patch plaster, redecoration after structural alterations
GROUP 8 — EXTERNAL WORKS
8 | 8.1 | Site preparation & clearance | Item | 16.92 | 15.0588 | 18.7812 | 7529.4 | 9390.6 | Strip topsoil, vegetation, temp fencing and hoarding
8 | 8.2 | Roads, paths & hard paving | m² | 32.9 | 29.281 | 36.519 | 14640.5 | 18259.5 | Macadam/block paving; inc edging and drainage channels
8 | 8.3 | Car parking (line-marked bays) | Nr | 11.28 | 10.0392 | 12.5208 | 5019.6 | 6260.4 | Surfacing, line markings, disabled bays
8 | 8.4 | Surface water drainage | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Gullies, pipes, SuDS if required by planning
8 | 8.5 | Foul drainage connections | Item | 14.1 | 12.549 | 15.651 | 6274.5 | 7825.5 | Connection to existing drain or new manhole
8 | 8.6 | External utility services | Item | 18.8 | 16.732 | 20.868 | 8366 | 10434 | Gas/water/electric diversions; early check with DNO
8 | 8.7 | Soft landscaping | m² | 11.28 | 10.0392 | 12.5208 | 5019.6 | 6260.4 | Planting, seeding, topsoil reinstatement
8 | 8.8 | Boundary enclosures (fences/gates) | Item | 9.4 | 8.366 | 10.434 | 4183 | 5217 | Security fencing, gates, boundary walls, railings
8 | 8.9 | External lighting | Item | 7.52 | 6.6928 | 8.3472 | 3346.4 | 4173.6 | Column or wall-mounted lighting (see also 5.10)
WORKS COST SUBTOTAL (Groups 0–8) | [6 empty] | 2719786.6 | 3392093.4
ADDITIONS TO WORKS COST — Adjust % using signal rules in Notes column
Code |  |  | Description | Applied To | Low % | High % | Total LOW (£) | Total HIGH (£) | Signal Rules / Notes
A |  |  | Contractor's Preliminaries | Works Cost | 8% | 10% | 217582.928 | 339209.34 | 8%=clean/vacant/short prog ¦ +0.5% per: 6-18mo prog, partial occ, restricted access ¦ cap 10%
B |  |  | Contractor's Overheads & Profit | Works Cost | 8% | 12% | 217582.928 | 407051.208 | >£5M→8-9% ¦ £1-5M→9-10% ¦ <£1M→10-12% ¦ Lower end = cost priority; upper = D&B/speed
CONSTRUCTION COST SUBTOTAL (Works + Prelims + OH&P) | [6 empty] | 3154952.456 | 4138353.948
C |  |  | Professional Fees | Construction Cost | 5% | 15% | 157747.6228 | 620753.0922 | Stage 0-1→12-15% ¦ Stage 2→10-13% ¦ Stage 3→7-10% ¦ Stage 4→5-7% ¦ +1-2% M&E/struct/BREEAM
D |  |  | Dev & Project Costs | Construction Cost | 2% | 4% | 63099.0491 | 165534.1579 | Full planning→3-4% ¦ LBC also→4% ¦ Permitted dev→2% ¦ +0.5% if no surveys yet
E |  |  | Risk Allowance | Works Cost | 5% | 10% | 135989.33 | 339209.34 | Baseline 5% ¦ +2% no surveys ¦ +1.5% asbestos/contamination ¦ +1% structural concern ¦ +1% hard deadline ¦ cap 10%
H |  |  | Client Contingency [FIXED 5%] | Works Cost | 5% | 5% | 135989.33 | 169604.67 | FIXED at 5% — held by client, not released to contractor. Do not adjust.
F |  |  | Inflation Allowance | Works Cost | 2% | 12% | 54395.732 | 407051.208 | Component 1: tender delay (0-18mo=2-6%) + Component 2: construction mid-point (6-24mo=1-4%) ¦ cap 12%
TOTAL PROJECT COST (excl. VAT) | [6 empty] | 3702173.5199 | 5840506.4161
G |  |  | VAT — reference only, NOT in total | Project Total | 20% | 20% | 740434.704 | 1168101.2832 | Recoverability must be confirmed with client Finance team. New build may attract zero-rating.
Implied blended Works Cost rate — cross-check against BCIS benchmarks: |  |  |  | 5439.5732 |  | 6784.1868
⚠ DISCLAIMER: Indicative only — RIBA Stage 0–1 without measured quantities. Rates from Rates Reference Table, cross-referenced Q2 2026 market data. Must be reviewed by a Chartered QS before use in any business case or budget approval. LOW–HIGH range = mid-point ± 11% (default spread 22%). Update GIFA, BCIS factor and Spread as required.

## Extension – Std
NRM1 ESTIMATE — EXTENSION — STANDARD
Spec level: Standard extension to existing building, matching existing spec and construction. ¦ RIBA Stage 0–1 indicative only ¦ Base date Q2 2026
Project Type: | Extension |  | Spec Level: | Standard |  | Region: | West Midlands
GIFA (m²) ▼ update: | 250 |  | BCIS Location Factor ▼: | 94% |  | Spread ±% ▼: | 22%
Grp | Sub | Element / Description | Unit | Mid-Point £/m² | Low £/m² | High £/m² | Total LOW (£) | Total HIGH (£) | Notes / Rate Driver
GROUP 0 — FACILITATING WORKS
0 | 0.1 | Toxic/hazardous material removal | Item | 9.4 | 8.366 | 10.434 | 2091.5 | 2608.5 | Asbestos; increase if confirmed present (refurb/demo only)
0 | 0.2 | Demolition & structural alterations | Item | 18.8 | 16.732 | 20.868 | 4183 | 5217 | Selective or full demolition; structural openings
0 | 0.3 | Contaminated land remediation | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Brownfield/contaminated; specialist quote needed
0 | 0.4 | Ground stabilisation | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Underpinning/piling if ground risk identified
GROUP 1 — SUBSTRUCTURE
1 | 1.1 | Standard foundations (strip/pad) | m² | 51.7 | 46.013 | 57.387 | 11503.25 | 14346.75 | New build only; included in Group 7 rate for extensions
1 | 1.2 | Specialist foundations (piled) | m² | 37.6 | 33.464 | 41.736 | 8366 | 10434 | Poor ground conditions; trigger from GI report
1 | 1.3 | Lowest floor construction (slab) | m² | 32.9 | 29.281 | 36.519 | 7320.25 | 9129.75 | Ground bearing or suspended; inc DPM and insulation
1 | 1.4 | Basement excavation & structure | Item | 75.2 | 66.928 | 83.472 | 16732 | 20868 | High uncertainty; specialist estimate recommended
GROUP 2 — SUPERSTRUCTURE
2 | 2.1 | Structural frame | m² | 122.2 | 108.758 | 135.642 | 27189.5 | 33910.5 | Steel/concrete/timber; new build or major extensions only
2 | 2.2 | Upper floors | m² | 61.1 | 54.379 | 67.821 | 13594.75 | 16955.25 | New build or added floors; inc topping and insulation
2 | 2.3 | Roof structure & covering | m² | 70.5 | 62.745 | 78.255 | 15686.25 | 19563.75 | New or replacement; inc insulation, waterproofing, rainwater
2 | 2.4 | Stairs & ramps | Item | 18.8 | 16.732 | 20.868 | 4183 | 5217 | RC, steel or timber; accessibility ramps
2 | 2.5 | External walls & facade | m² | 169.2 | 150.588 | 187.812 | 37647 | 46953 | Masonry/cladding; refurb = overcladding or repair only
2 | 2.6 | Windows & external doors | m² | 84.6 | 75.294 | 93.906 | 18823.5 | 23476.5 | uPVC (low) to aluminium curtain wall (high)
2 | 2.7 | Internal walls & partitions | m² | 23.5 | 20.915 | 26.085 | 5228.75 | 6521.25 | Blockwork, drywall or glazed; do not double-count Grp 3
2 | 2.8 | Internal doors & ironmongery | Nr | 16.92 | 15.0588 | 18.7812 | 3764.7 | 4695.3 | Fire-rated at upper range; standard at lower
GROUP 3 — INTERNAL FINISHES ★ ALWAYS INCLUDED
3 | 3.1 | Wall finishes | m² | 18.8 | 16.732 | 20.868 | 4183 | 5217 | Emulsion (low) → specialist tiling/feature panelling (high)
3 | 3.2 | Floor finishes | m² | 23.5 | 20.915 | 26.085 | 5228.75 | 6521.25 | Vinyl/carpet (low) → stone/raised access floor (high)
3 | 3.3 | Ceiling finishes | m² | 11.28 | 10.0392 | 12.5208 | 2509.8 | 3130.2 | Emulsion (low) → bespoke acoustic ceiling system (high)
GROUP 4 — FITTINGS, FURNISHINGS & EQUIPMENT
4 | 4.1 | General fittings & built-in joinery | Item | 9.4 | 8.366 | 10.434 | 2091.5 | 2608.5 | Reception desks, shelving, built-in furniture
4 | 4.2 | Sanitary fittings & toilet fit-out | Nr | 7.52 | 6.6928 | 8.3472 | 1673.2 | 2086.8 | WC packs; uplift for accessible/changing facilities
4 | 4.3 | Kitchen / break-out area | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Fitted units, worktops, appliances
4 | 4.4 | Specialist equipment (lab/AV/med) | Item | 0 | 0 | 0 | 0 | 0 | Laboratory, medical, AV; confirm with specialist
GROUP 5 — MECHANICAL & ELECTRICAL SERVICES ★ KEY ELEMENT
5 | 5.1 | Sanitary plumbing (1st & 2nd fix) | m² | 18.8 | 16.732 | 20.868 | 4183 | 5217 | HWS, cold water, drainage connections
5 | 5.2 | Heating & hot water (LTHW/heat pump) | m² | 28.2 | 25.098 | 31.302 | 6274.5 | 7825.5 | LTHW system or heat pump; include buffer vessel
5 | 5.3 | Ventilation & air handling | m² | 23.5 | 20.915 | 26.085 | 5228.75 | 6521.25 | MVHR/AHU; uplift for lab/healthcare extract (+50-100%)
5 | 5.4 | Air conditioning & cooling | m² | 9.4 | 8.366 | 10.434 | 2091.5 | 2608.5 | VRF/splits; omit if not in scope
5 | 5.5 | Gas installation | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Omit if all-electric; confirm with utility
5 | 5.6 | Sprinkler / fire suppression | m² | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | >18m height or insurer requirement
5 | 5.7 | Electrical distribution & switchgear | m² | 14.1 | 12.549 | 15.651 | 3137.25 | 3912.75 | LV panels, distribution boards, earthing, containment
5 | 5.8 | Electrical wiring (1st & 2nd fix) | m² | 23.5 | 20.915 | 26.085 | 5228.75 | 6521.25 | All power and lighting circuits; inc containment
5 | 5.9 | Emergency lighting & fire alarm | m² | 9.4 | 8.366 | 10.434 | 2091.5 | 2608.5 | L2 minimum; upgrade for multi-zone/complex layouts
5 | 5.10 | External lighting | Item | 2.82 | 2.5098 | 3.1302 | 627.45 | 782.55 | Column/wall-mounted perimeter lighting
5 | 5.11 | Solar PV / renewables | kWp | 752 | 669.28 | 834.72 | 167320 | 208680 | £/kWp installed; coordinate structural loading + electrical
5 | 5.12 | EV charging points | Nr | 1410 | 1254.9 | 1565.1 | 313725 | 391275 | Per charge point inc groundworks; 7kW fast charger
5 | 5.13 | IT / data infrastructure (Cat6A) | m² | 7.52 | 6.6928 | 8.3472 | 1673.2 | 2086.8 | Cabling, containment, patch panels
5 | 5.14 | AV systems | Item | 2.82 | 2.5098 | 3.1302 | 627.45 | 782.55 | Lecture rooms, boardrooms; specialist-designed
5 | 5.15 | Access control & CCTV / security | m² | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Door access readers, CCTV; varies by security level
5 | 5.16 | Lifts & platform lifts | Nr | 47 | 41.83 | 52.17 | 10457.5 | 13042.5 | Per installation × Nr; inc shaft if new build
5 | 5.17 | Builder's work in connection (BWIC) | m² | 5.64 | 5.0196 | 6.2604 | 1254.9 | 1565.1 | Penetrations, plinths, ducts, concrete bases for plant
GROUP 6 — PREFABRICATED / MODULAR (if applicable)
6 | 6.1 | Prefabricated / modular units | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Factory-built modular; specialist quote required
6 | 6.2 | Pre-engineered systems (mezzanine) | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Mezzanine floors, demountable partitions
GROUP 7 — WORK TO EXISTING BUILDINGS
7 | 7.1 | Structural repairs | Item | 14.1 | 12.549 | 15.651 | 3137.25 | 3912.75 | Crack stitching, bearing repairs; increase for poor condition
7 | 7.2 | Fabric / envelope repairs | Item | 11.28 | 10.0392 | 12.5208 | 2509.8 | 3130.2 | Repointing, waterproofing, weathertight works
7 | 7.3 | Damp proof course treatment | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Chemical DPC; increase for severe rising damp
7 | 7.4 | M&E overhaul / life-expired services | Item | 18.8 | 16.732 | 20.868 | 4183 | 5217 | Replacement of end-of-life mechanical & electrical plant
7 | 7.5 | Making good after structural works | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Patch plaster, redecoration after structural alterations
GROUP 8 — EXTERNAL WORKS
8 | 8.1 | Site preparation & clearance | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Strip topsoil, vegetation, temp fencing and hoarding
8 | 8.2 | Roads, paths & hard paving | m² | 9.4 | 8.366 | 10.434 | 2091.5 | 2608.5 | Macadam/block paving; inc edging and drainage channels
8 | 8.3 | Car parking (line-marked bays) | Nr | 2.82 | 2.5098 | 3.1302 | 627.45 | 782.55 | Surfacing, line markings, disabled bays
8 | 8.4 | Surface water drainage | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Gullies, pipes, SuDS if required by planning
8 | 8.5 | Foul drainage connections | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Connection to existing drain or new manhole
8 | 8.6 | External utility services | Item | 4.7 | 4.183 | 5.217 | 1045.75 | 1304.25 | Gas/water/electric diversions; early check with DNO
8 | 8.7 | Soft landscaping | m² | 2.82 | 2.5098 | 3.1302 | 627.45 | 782.55 | Planting, seeding, topsoil reinstatement
8 | 8.8 | Boundary enclosures (fences/gates) | Item | 1.88 | 1.6732 | 2.0868 | 418.3 | 521.7 | Security fencing, gates, boundary walls, railings
8 | 8.9 | External lighting | Item | 1.88 | 1.6732 | 2.0868 | 418.3 | 521.7 | Column or wall-mounted lighting (see also 5.10)
WORKS COST SUBTOTAL (Groups 0–8) | [6 empty] | 742482.5 | 926017.5
ADDITIONS TO WORKS COST — Adjust % using signal rules in Notes column
Code |  |  | Description | Applied To | Low % | High % | Total LOW (£) | Total HIGH (£) | Signal Rules / Notes
A |  |  | Contractor's Preliminaries | Works Cost | 8% | 10% | 59398.6 | 92601.75 | 8%=clean/vacant/short prog ¦ +0.5% per: 6-18mo prog, partial occ, restricted access ¦ cap 10%
B |  |  | Contractor's Overheads & Profit | Works Cost | 8% | 12% | 59398.6 | 111122.1 | >£5M→8-9% ¦ £1-5M→9-10% ¦ <£1M→10-12% ¦ Lower end = cost priority; upper = D&B/speed
CONSTRUCTION COST SUBTOTAL (Works + Prelims + OH&P) | [6 empty] | 861279.7 | 1129741.35
C |  |  | Professional Fees | Construction Cost | 5% | 15% | 43063.985 | 169461.2025 | Stage 0-1→12-15% ¦ Stage 2→10-13% ¦ Stage 3→7-10% ¦ Stage 4→5-7% ¦ +1-2% M&E/struct/BREEAM
D |  |  | Dev & Project Costs | Construction Cost | 2% | 4% | 17225.594 | 45189.654 | Full planning→3-4% ¦ LBC also→4% ¦ Permitted dev→2% ¦ +0.5% if no surveys yet
E |  |  | Risk Allowance | Works Cost | 5% | 10% | 37124.125 | 92601.75 | Baseline 5% ¦ +2% no surveys ¦ +1.5% asbestos/contamination ¦ +1% structural concern ¦ +1% hard deadline ¦ cap 10%
H |  |  | Client Contingency [FIXED 5%] | Works Cost | 5% | 5% | 37124.125 | 46300.875 | FIXED at 5% — held by client, not released to contractor. Do not adjust.
F |  |  | Inflation Allowance | Works Cost | 2% | 12% | 14849.65 | 111122.1 | Component 1: tender delay (0-18mo=2-6%) + Component 2: construction mid-point (6-24mo=1-4%) ¦ cap 12%
TOTAL PROJECT COST (excl. VAT) | [6 empty] | 1010667.179 | 1594416.9315
G |  |  | VAT — reference only, NOT in total | Project Total | 20% | 20% | 202133.4358 | 318883.3863 | Recoverability must be confirmed with client Finance team. New build may attract zero-rating.
Implied blended Works Cost rate — cross-check against BCIS benchmarks: |  |  |  | 2969.93 |  | 3704.07
⚠ DISCLAIMER: Indicative only — RIBA Stage 0–1 without measured quantities. Rates from Rates Reference Table, cross-referenced Q2 2026 market data. Must be reviewed by a Chartered QS before use in any business case or budget approval. LOW–HIGH range = mid-point ± 11% (default spread 22%). Update GIFA, BCIS factor and Spread as required.

## Extension – High
NRM1 ESTIMATE — EXTENSION — HIGH SPEC
Spec level: High-spec or technically complex extension (lab, glazed atrium, bespoke facade). ¦ RIBA Stage 0–1 indicative only ¦ Base date Q2 2026
Project Type: | Extension |  | Spec Level: | High Spec |  | Region: | West Midlands
GIFA (m²) ▼ update: | 250 |  | BCIS Location Factor ▼: | 94% |  | Spread ±% ▼: | 22%
Grp | Sub | Element / Description | Unit | Mid-Point £/m² | Low £/m² | High £/m² | Total LOW (£) | Total HIGH (£) | Notes / Rate Driver
GROUP 0 — FACILITATING WORKS
0 | 0.1 | Toxic/hazardous material removal | Item | 18.8 | 16.732 | 20.868 | 4183 | 5217 | Asbestos; increase if confirmed present (refurb/demo only)
0 | 0.2 | Demolition & structural alterations | Item | 32.9 | 29.281 | 36.519 | 7320.25 | 9129.75 | Selective or full demolition; structural openings
0 | 0.3 | Contaminated land remediation | Item | 14.1 | 12.549 | 15.651 | 3137.25 | 3912.75 | Brownfield/contaminated; specialist quote needed
0 | 0.4 | Ground stabilisation | Item | 11.28 | 10.0392 | 12.5208 | 2509.8 | 3130.2 | Underpinning/piling if ground risk identified
GROUP 1 — SUBSTRUCTURE
1 | 1.1 | Standard foundations (strip/pad) | m² | 75.2 | 66.928 | 83.472 | 16732 | 20868 | New build only; included in Group 7 rate for extensions
1 | 1.2 | Specialist foundations (piled) | m² | 56.4 | 50.196 | 62.604 | 12549 | 15651 | Poor ground conditions; trigger from GI report
1 | 1.3 | Lowest floor construction (slab) | m² | 51.7 | 46.013 | 57.387 | 11503.25 | 14346.75 | Ground bearing or suspended; inc DPM and insulation
1 | 1.4 | Basement excavation & structure | Item | 141 | 125.49 | 156.51 | 31372.5 | 39127.5 | High uncertainty; specialist estimate recommended
GROUP 2 — SUPERSTRUCTURE
2 | 2.1 | Structural frame | m² | 188 | 167.32 | 208.68 | 41830 | 52170 | Steel/concrete/timber; new build or major extensions only
2 | 2.2 | Upper floors | m² | 89.3 | 79.477 | 99.123 | 19869.25 | 24780.75 | New build or added floors; inc topping and insulation
2 | 2.3 | Roof structure & covering | m² | 112.8 | 100.392 | 125.208 | 25098 | 31302 | New or replacement; inc insulation, waterproofing, rainwater
2 | 2.4 | Stairs & ramps | Item | 32.9 | 29.281 | 36.519 | 7320.25 | 9129.75 | RC, steel or timber; accessibility ramps
2 | 2.5 | External walls & facade | m² | 263.2 | 234.248 | 292.152 | 58562 | 73038 | Masonry/cladding; refurb = overcladding or repair only
2 | 2.6 | Windows & external doors | m² | 141 | 125.49 | 156.51 | 31372.5 | 39127.5 | uPVC (low) to aluminium curtain wall (high)
2 | 2.7 | Internal walls & partitions | m² | 42.3 | 37.647 | 46.953 | 9411.75 | 11738.25 | Blockwork, drywall or glazed; do not double-count Grp 3
2 | 2.8 | Internal doors & ironmongery | Nr | 28.2 | 25.098 | 31.302 | 6274.5 | 7825.5 | Fire-rated at upper range; standard at lower
GROUP 3 — INTERNAL FINISHES ★ ALWAYS INCLUDED
3 | 3.1 | Wall finishes | m² | 47 | 41.83 | 52.17 | 10457.5 | 13042.5 | Emulsion (low) → specialist tiling/feature panelling (high)
3 | 3.2 | Floor finishes | m² | 65.8 | 58.562 | 73.038 | 14640.5 | 18259.5 | Vinyl/carpet (low) → stone/raised access floor (high)
3 | 3.3 | Ceiling finishes | m² | 37.6 | 33.464 | 41.736 | 8366 | 10434 | Emulsion (low) → bespoke acoustic ceiling system (high)
GROUP 4 — FITTINGS, FURNISHINGS & EQUIPMENT
4 | 4.1 | General fittings & built-in joinery | Item | 37.6 | 33.464 | 41.736 | 8366 | 10434 | Reception desks, shelving, built-in furniture
4 | 4.2 | Sanitary fittings & toilet fit-out | Nr | 16.92 | 15.0588 | 18.7812 | 3764.7 | 4695.3 | WC packs; uplift for accessible/changing facilities
4 | 4.3 | Kitchen / break-out area | Item | 14.1 | 12.549 | 15.651 | 3137.25 | 3912.75 | Fitted units, worktops, appliances
4 | 4.4 | Specialist equipment (lab/AV/med) | Item | 37.6 | 33.464 | 41.736 | 8366 | 10434 | Laboratory, medical, AV; confirm with specialist
GROUP 5 — MECHANICAL & ELECTRICAL SERVICES ★ KEY ELEMENT
5 | 5.1 | Sanitary plumbing (1st & 2nd fix) | m² | 42.3 | 37.647 | 46.953 | 9411.75 | 11738.25 | HWS, cold water, drainage connections
5 | 5.2 | Heating & hot water (LTHW/heat pump) | m² | 61.1 | 54.379 | 67.821 | 13594.75 | 16955.25 | LTHW system or heat pump; include buffer vessel
5 | 5.3 | Ventilation & air handling | m² | 56.4 | 50.196 | 62.604 | 12549 | 15651 | MVHR/AHU; uplift for lab/healthcare extract (+50-100%)
5 | 5.4 | Air conditioning & cooling | m² | 42.3 | 37.647 | 46.953 | 9411.75 | 11738.25 | VRF/splits; omit if not in scope
5 | 5.5 | Gas installation | Item | 9.4 | 8.366 | 10.434 | 2091.5 | 2608.5 | Omit if all-electric; confirm with utility
5 | 5.6 | Sprinkler / fire suppression | m² | 18.8 | 16.732 | 20.868 | 4183 | 5217 | >18m height or insurer requirement
5 | 5.7 | Electrical distribution & switchgear | m² | 37.6 | 33.464 | 41.736 | 8366 | 10434 | LV panels, distribution boards, earthing, containment
5 | 5.8 | Electrical wiring (1st & 2nd fix) | m² | 51.7 | 46.013 | 57.387 | 11503.25 | 14346.75 | All power and lighting circuits; inc containment
5 | 5.9 | Emergency lighting & fire alarm | m² | 20.68 | 18.4052 | 22.9548 | 4601.3 | 5738.7 | L2 minimum; upgrade for multi-zone/complex layouts
5 | 5.10 | External lighting | Item | 7.52 | 6.6928 | 8.3472 | 1673.2 | 2086.8 | Column/wall-mounted perimeter lighting
5 | 5.11 | Solar PV / renewables | kWp | 1128 | 1003.92 | 1252.08 | 250980 | 313020 | £/kWp installed; coordinate structural loading + electrical
5 | 5.12 | EV charging points | Nr | 2350 | 2091.5 | 2608.5 | 522875 | 652125 | Per charge point inc groundworks; 7kW fast charger
5 | 5.13 | IT / data infrastructure (Cat6A) | m² | 18.8 | 16.732 | 20.868 | 4183 | 5217 | Cabling, containment, patch panels
5 | 5.14 | AV systems | Item | 28.2 | 25.098 | 31.302 | 6274.5 | 7825.5 | Lecture rooms, boardrooms; specialist-designed
5 | 5.15 | Access control & CCTV / security | m² | 14.1 | 12.549 | 15.651 | 3137.25 | 3912.75 | Door access readers, CCTV; varies by security level
5 | 5.16 | Lifts & platform lifts | Nr | 84.6 | 75.294 | 93.906 | 18823.5 | 23476.5 | Per installation × Nr; inc shaft if new build
5 | 5.17 | Builder's work in connection (BWIC) | m² | 14.1 | 12.549 | 15.651 | 3137.25 | 3912.75 | Penetrations, plinths, ducts, concrete bases for plant
GROUP 6 — PREFABRICATED / MODULAR (if applicable)
6 | 6.1 | Prefabricated / modular units | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Factory-built modular; specialist quote required
6 | 6.2 | Pre-engineered systems (mezzanine) | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Mezzanine floors, demountable partitions
GROUP 7 — WORK TO EXISTING BUILDINGS
7 | 7.1 | Structural repairs | Item | 32.9 | 29.281 | 36.519 | 7320.25 | 9129.75 | Crack stitching, bearing repairs; increase for poor condition
7 | 7.2 | Fabric / envelope repairs | Item | 26.32 | 23.4248 | 29.2152 | 5856.2 | 7303.8 | Repointing, waterproofing, weathertight works
7 | 7.3 | Damp proof course treatment | Item | 14.1 | 12.549 | 15.651 | 3137.25 | 3912.75 | Chemical DPC; increase for severe rising damp
7 | 7.4 | M&E overhaul / life-expired services | Item | 51.7 | 46.013 | 57.387 | 11503.25 | 14346.75 | Replacement of end-of-life mechanical & electrical plant
7 | 7.5 | Making good after structural works | Item | 11.28 | 10.0392 | 12.5208 | 2509.8 | 3130.2 | Patch plaster, redecoration after structural alterations
GROUP 8 — EXTERNAL WORKS
8 | 8.1 | Site preparation & clearance | Item | 11.28 | 10.0392 | 12.5208 | 2509.8 | 3130.2 | Strip topsoil, vegetation, temp fencing and hoarding
8 | 8.2 | Roads, paths & hard paving | m² | 23.5 | 20.915 | 26.085 | 5228.75 | 6521.25 | Macadam/block paving; inc edging and drainage channels
8 | 8.3 | Car parking (line-marked bays) | Nr | 7.52 | 6.6928 | 8.3472 | 1673.2 | 2086.8 | Surfacing, line markings, disabled bays
8 | 8.4 | Surface water drainage | Item | 14.1 | 12.549 | 15.651 | 3137.25 | 3912.75 | Gullies, pipes, SuDS if required by planning
8 | 8.5 | Foul drainage connections | Item | 9.4 | 8.366 | 10.434 | 2091.5 | 2608.5 | Connection to existing drain or new manhole
8 | 8.6 | External utility services | Item | 14.1 | 12.549 | 15.651 | 3137.25 | 3912.75 | Gas/water/electric diversions; early check with DNO
8 | 8.7 | Soft landscaping | m² | 9.4 | 8.366 | 10.434 | 2091.5 | 2608.5 | Planting, seeding, topsoil reinstatement
8 | 8.8 | Boundary enclosures (fences/gates) | Item | 7.52 | 6.6928 | 8.3472 | 1673.2 | 2086.8 | Security fencing, gates, boundary walls, railings
8 | 8.9 | External lighting | Item | 5.64 | 5.0196 | 6.2604 | 1254.9 | 1565.1 | Column or wall-mounted lighting (see also 5.10)
WORKS COST SUBTOTAL (Groups 0–8) | [6 empty] | 1286063.35 | 1603966.65
ADDITIONS TO WORKS COST — Adjust % using signal rules in Notes column
Code |  |  | Description | Applied To | Low % | High % | Total LOW (£) | Total HIGH (£) | Signal Rules / Notes
A |  |  | Contractor's Preliminaries | Works Cost | 8% | 10% | 102885.068 | 160396.665 | 8%=clean/vacant/short prog ¦ +0.5% per: 6-18mo prog, partial occ, restricted access ¦ cap 10%
B |  |  | Contractor's Overheads & Profit | Works Cost | 8% | 12% | 102885.068 | 192475.998 | >£5M→8-9% ¦ £1-5M→9-10% ¦ <£1M→10-12% ¦ Lower end = cost priority; upper = D&B/speed
CONSTRUCTION COST SUBTOTAL (Works + Prelims + OH&P) | [6 empty] | 1491833.486 | 1956839.313
C |  |  | Professional Fees | Construction Cost | 5% | 15% | 74591.6743 | 293525.897 | Stage 0-1→12-15% ¦ Stage 2→10-13% ¦ Stage 3→7-10% ¦ Stage 4→5-7% ¦ +1-2% M&E/struct/BREEAM
D |  |  | Dev & Project Costs | Construction Cost | 2% | 4% | 29836.6697 | 78273.5725 | Full planning→3-4% ¦ LBC also→4% ¦ Permitted dev→2% ¦ +0.5% if no surveys yet
E |  |  | Risk Allowance | Works Cost | 5% | 10% | 64303.1675 | 160396.665 | Baseline 5% ¦ +2% no surveys ¦ +1.5% asbestos/contamination ¦ +1% structural concern ¦ +1% hard deadline ¦ cap 10%
H |  |  | Client Contingency [FIXED 5%] | Works Cost | 5% | 5% | 64303.1675 | 80198.3325 | FIXED at 5% — held by client, not released to contractor. Do not adjust.
F |  |  | Inflation Allowance | Works Cost | 2% | 12% | 25721.267 | 192475.998 | Component 1: tender delay (0-18mo=2-6%) + Component 2: construction mid-point (6-24mo=1-4%) ¦ cap 12%
TOTAL PROJECT COST (excl. VAT) | [6 empty] | 1750589.432 | 2761709.778
G |  |  | VAT — reference only, NOT in total | Project Total | 20% | 20% | 350117.8864 | 552341.9556 | Recoverability must be confirmed with client Finance team. New build may attract zero-rating.
Implied blended Works Cost rate — cross-check against BCIS benchmarks: |  |  |  | 5144.2534 |  | 6415.8666
⚠ DISCLAIMER: Indicative only — RIBA Stage 0–1 without measured quantities. Rates from Rates Reference Table, cross-referenced Q2 2026 market data. Must be reviewed by a Chartered QS before use in any business case or budget approval. LOW–HIGH range = mid-point ± 11% (default spread 22%). Update GIFA, BCIS factor and Spread as required.

## External Works
NRM1 ESTIMATE — EXTERNAL WORKS — SITE WORKS
Spec level: Site-only works: roads, parking, drainage, landscaping, utilities, lighting. ¦ RIBA Stage 0–1 indicative only ¦ Base date Q2 2026
Project Type: | External Works |  | Spec Level: | Site Works |  | Region: | West Midlands
GIFA (m²) ▼ update: | 1000 |  | BCIS Location Factor ▼: | 94% |  | Spread ±% ▼: | 22%
Grp | Sub | Element / Description | Unit | Mid-Point £/m² | Low £/m² | High £/m² | Total LOW (£) | Total HIGH (£) | Notes / Rate Driver
GROUP 0 — FACILITATING WORKS
0 | 0.1 | Toxic/hazardous material removal | Item | 0 | 0 | 0 | 0 | 0 | Asbestos; increase if confirmed present (refurb/demo only)
0 | 0.2 | Demolition & structural alterations | Item | 4.7 | 4.183 | 5.217 | 4183 | 5217 | Selective or full demolition; structural openings
0 | 0.3 | Contaminated land remediation | Item | 9.4 | 8.366 | 10.434 | 8366 | 10434 | Brownfield/contaminated; specialist quote needed
0 | 0.4 | Ground stabilisation | Item | 4.7 | 4.183 | 5.217 | 4183 | 5217 | Underpinning/piling if ground risk identified
GROUP 1 — SUBSTRUCTURE
1 | 1.1 | Standard foundations (strip/pad) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | New build only; included in Group 7 rate for extensions
1 | 1.2 | Specialist foundations (piled) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Poor ground conditions; trigger from GI report
1 | 1.3 | Lowest floor construction (slab) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Ground bearing or suspended; inc DPM and insulation
1 | 1.4 | Basement excavation & structure | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | High uncertainty; specialist estimate recommended
GROUP 2 — SUPERSTRUCTURE
2 | 2.1 | Structural frame | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Steel/concrete/timber; new build or major extensions only
2 | 2.2 | Upper floors | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | New build or added floors; inc topping and insulation
2 | 2.3 | Roof structure & covering | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | New or replacement; inc insulation, waterproofing, rainwater
2 | 2.4 | Stairs & ramps | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | RC, steel or timber; accessibility ramps
2 | 2.5 | External walls & facade | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Masonry/cladding; refurb = overcladding or repair only
2 | 2.6 | Windows & external doors | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | uPVC (low) to aluminium curtain wall (high)
2 | 2.7 | Internal walls & partitions | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Blockwork, drywall or glazed; do not double-count Grp 3
2 | 2.8 | Internal doors & ironmongery | Nr | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Fire-rated at upper range; standard at lower
GROUP 3 — INTERNAL FINISHES ★ ALWAYS INCLUDED
3 | 3.1 | Wall finishes | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Emulsion (low) → specialist tiling/feature panelling (high)
3 | 3.2 | Floor finishes | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Vinyl/carpet (low) → stone/raised access floor (high)
3 | 3.3 | Ceiling finishes | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Emulsion (low) → bespoke acoustic ceiling system (high)
GROUP 4 — FITTINGS, FURNISHINGS & EQUIPMENT
4 | 4.1 | General fittings & built-in joinery | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Reception desks, shelving, built-in furniture
4 | 4.2 | Sanitary fittings & toilet fit-out | Nr | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | WC packs; uplift for accessible/changing facilities
4 | 4.3 | Kitchen / break-out area | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Fitted units, worktops, appliances
4 | 4.4 | Specialist equipment (lab/AV/med) | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Laboratory, medical, AV; confirm with specialist
GROUP 5 — MECHANICAL & ELECTRICAL SERVICES ★ KEY ELEMENT
5 | 5.1 | Sanitary plumbing (1st & 2nd fix) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | HWS, cold water, drainage connections
5 | 5.2 | Heating & hot water (LTHW/heat pump) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | LTHW system or heat pump; include buffer vessel
5 | 5.3 | Ventilation & air handling | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | MVHR/AHU; uplift for lab/healthcare extract (+50-100%)
5 | 5.4 | Air conditioning & cooling | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | VRF/splits; omit if not in scope
5 | 5.5 | Gas installation | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Omit if all-electric; confirm with utility
5 | 5.6 | Sprinkler / fire suppression | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | >18m height or insurer requirement
5 | 5.7 | Electrical distribution & switchgear | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | LV panels, distribution boards, earthing, containment
5 | 5.8 | Electrical wiring (1st & 2nd fix) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | All power and lighting circuits; inc containment
5 | 5.9 | Emergency lighting & fire alarm | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | L2 minimum; upgrade for multi-zone/complex layouts
5 | 5.10 | External lighting | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Column/wall-mounted perimeter lighting
5 | 5.11 | Solar PV / renewables | kWp | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | £/kWp installed; coordinate structural loading + electrical
5 | 5.12 | EV charging points | Nr | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Per charge point inc groundworks; 7kW fast charger
5 | 5.13 | IT / data infrastructure (Cat6A) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Cabling, containment, patch panels
5 | 5.14 | AV systems | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Lecture rooms, boardrooms; specialist-designed
5 | 5.15 | Access control & CCTV / security | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Door access readers, CCTV; varies by security level
5 | 5.16 | Lifts & platform lifts | Nr | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Per installation × Nr; inc shaft if new build
5 | 5.17 | Builder's work in connection (BWIC) | m² | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Penetrations, plinths, ducts, concrete bases for plant
GROUP 6 — PREFABRICATED / MODULAR (if applicable)
6 | 6.1 | Prefabricated / modular units | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Factory-built modular; specialist quote required
6 | 6.2 | Pre-engineered systems (mezzanine) | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Mezzanine floors, demountable partitions
GROUP 7 — WORK TO EXISTING BUILDINGS
7 | 7.1 | Structural repairs | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Crack stitching, bearing repairs; increase for poor condition
7 | 7.2 | Fabric / envelope repairs | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Repointing, waterproofing, weathertight works
7 | 7.3 | Damp proof course treatment | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Chemical DPC; increase for severe rising damp
7 | 7.4 | M&E overhaul / life-expired services | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Replacement of end-of-life mechanical & electrical plant
7 | 7.5 | Making good after structural works | Item | EXCLUDED | EXCLUDED | EXCLUDED | 0 | 0 | Patch plaster, redecoration after structural alterations
GROUP 8 — EXTERNAL WORKS
8 | 8.1 | Site preparation & clearance | Item | 9.4 | 8.366 | 10.434 | 8366 | 10434 | Strip topsoil, vegetation, temp fencing and hoarding
8 | 8.2 | Roads, paths & hard paving | m² | 32.9 | 29.281 | 36.519 | 29281 | 36519 | Macadam/block paving; inc edging and drainage channels
8 | 8.3 | Car parking (line-marked bays) | Nr | 18.8 | 16.732 | 20.868 | 16732 | 20868 | Surfacing, line markings, disabled bays
8 | 8.4 | Surface water drainage | Item | 23.5 | 20.915 | 26.085 | 20915 | 26085 | Gullies, pipes, SuDS if required by planning
8 | 8.5 | Foul drainage connections | Item | 14.1 | 12.549 | 15.651 | 12549 | 15651 | Connection to existing drain or new manhole
8 | 8.6 | External utility services | Item | 18.8 | 16.732 | 20.868 | 16732 | 20868 | Gas/water/electric diversions; early check with DNO
8 | 8.7 | Soft landscaping | m² | 14.1 | 12.549 | 15.651 | 12549 | 15651 | Planting, seeding, topsoil reinstatement
8 | 8.8 | Boundary enclosures (fences/gates) | Item | 11.28 | 10.0392 | 12.5208 | 10039.2 | 12520.8 | Security fencing, gates, boundary walls, railings
8 | 8.9 | External lighting | Item | 9.4 | 8.366 | 10.434 | 8366 | 10434 | Column or wall-mounted lighting (see also 5.10)
WORKS COST SUBTOTAL (Groups 0–8) | [6 empty] | 152261.2 | 189898.8
ADDITIONS TO WORKS COST — Adjust % using signal rules in Notes column
Code |  |  | Description | Applied To | Low % | High % | Total LOW (£) | Total HIGH (£) | Signal Rules / Notes
A |  |  | Contractor's Preliminaries | Works Cost | 8% | 10% | 12180.896 | 18989.88 | 8%=clean/vacant/short prog ¦ +0.5% per: 6-18mo prog, partial occ, restricted access ¦ cap 10%
B |  |  | Contractor's Overheads & Profit | Works Cost | 8% | 12% | 12180.896 | 22787.856 | >£5M→8-9% ¦ £1-5M→9-10% ¦ <£1M→10-12% ¦ Lower end = cost priority; upper = D&B/speed
CONSTRUCTION COST SUBTOTAL (Works + Prelims + OH&P) | [6 empty] | 176622.992 | 231676.536
C |  |  | Professional Fees | Construction Cost | 5% | 15% | 8831.1496 | 34751.4804 | Stage 0-1→12-15% ¦ Stage 2→10-13% ¦ Stage 3→7-10% ¦ Stage 4→5-7% ¦ +1-2% M&E/struct/BREEAM
D |  |  | Dev & Project Costs | Construction Cost | 2% | 4% | 3532.4598 | 9267.0614 | Full planning→3-4% ¦ LBC also→4% ¦ Permitted dev→2% ¦ +0.5% if no surveys yet
E |  |  | Risk Allowance | Works Cost | 5% | 10% | 7613.06 | 18989.88 | Baseline 5% ¦ +2% no surveys ¦ +1.5% asbestos/contamination ¦ +1% structural concern ¦ +1% hard deadline ¦ cap 10%
H |  |  | Client Contingency [FIXED 5%] | Works Cost | 5% | 5% | 7613.06 | 9494.94 | FIXED at 5% — held by client, not released to contractor. Do not adjust.
F |  |  | Inflation Allowance | Works Cost | 2% | 12% | 3045.224 | 22787.856 | Component 1: tender delay (0-18mo=2-6%) + Component 2: construction mid-point (6-24mo=1-4%) ¦ cap 12%
TOTAL PROJECT COST (excl. VAT) | [6 empty] | 207257.9454 | 326967.7538
G |  |  | VAT — reference only, NOT in total | Project Total | 20% | 20% | 41451.5891 | 65393.5508 | Recoverability must be confirmed with client Finance team. New build may attract zero-rating.
Implied blended Works Cost rate — cross-check against BCIS benchmarks: |  |  |  | 152.2612 |  | 189.8988
⚠ DISCLAIMER: Indicative only — RIBA Stage 0–1 without measured quantities. Rates from Rates Reference Table, cross-referenced Q2 2026 market data. Must be reviewed by a Chartered QS before use in any business case or budget approval. LOW–HIGH range = mid-point ± 11% (default spread 22%). Update GIFA, BCIS factor and Spread as required.

## BCIS Factors
BCIS REGIONAL LOCATION FACTORS — Q2 2026 Indicative
Region | Low Factor | High Factor | Notes
Inner London | 1.2 | 1.3 | Central London boroughs; highest UK cost premium
Outer London | 1.1 | 1.2 | Greater London boroughs
South East | 1.05 | 1.12 | Kent, Surrey, Berkshire, Hampshire, Sussex, Oxfordshire
East of England | 1 | 1.05 | Essex, Hertfordshire, Cambridgeshire, Norfolk, Suffolk
West Midlands | 0.92 | 0.97 | Birmingham, Coventry, Warwickshire ★ DEFAULT for this tool
East Midlands | 0.91 | 0.96 | Leicestershire, Nottinghamshire, Derbyshire
Yorkshire & Humberside | 0.88 | 0.93 | Leeds, Sheffield, Hull, York
North West | 0.9 | 0.95 | Manchester, Liverpool, Cheshire, Lancashire
North East | 0.87 | 0.92 | Newcastle, Sunderland, Teesside
Wales | 0.87 | 0.93 | All Welsh regions; Cardiff at upper end
Scotland | 0.93 | 1 | Edinburgh and central belt; Highlands higher
Northern Ireland | 0.82 | 0.88 | Belfast and Northern Ireland — lowest UK factor
USE MID-POINT: For a single-factor estimate use the average of Low and High factors shown. Example: West Midlands = (0.92+0.97)/2 = 0.945 → enter 0.94 in the estimate tab. Source: BCIS Location Factors; broadly stable year-on-year. Update if BCIS publishes revised regional indices.